{"text_format":"1","workbook":"xlsx","n_sheets":9,"sheets":["1.DADES","2.CLIMA","3.TERRENY","4.CONDUCTES","5.CÀLCUL","PARÀMETRES","TAULES","GRÀFICA","DITA"],"not_rendered":{"charts":4,"images":3,"macros":1,"external_links":0,"defined_names":3,"comments":0,"pivot_tables":1},"unopened":[],"bounds":{"document_bytes":16777216,"sheet_cells":100000,"rows_first":2000,"rows_last":500,"rows_between":2000,"halvings":0,"cell_chars":16384,"cell_head_chars":4096},"cells_cut":0,"cells_raw":0,"read":"whole","date_system":"1900"}

{"sheet":"1.DADES","index":0,"n_rows":25,"n_cols":1,"rows_kept":25,"cut":false,"hidden":false,"merged":[[24,2,28,9],[11,2,12,9],[17,2,18,9],[0,0,0,10],[7,2,7,9],[9,2,9,9],[21,2,21,9],[15,2,15,9]]}
["DIMENSIONAMENT INTERCANVIADOR DE TERRA - AIRE | DITA"]
[]
["1. INFORMACIÓ DEL PROJECTE"]
[]
["Dades Generals"]
[]
[]
["     Ref.Projecte"]
[]
["     Projecte"]
[]
["     Localització"]
[]
[]
[]
["     Propietat"]
[]
["     Direcció"]
[]
[]
[]
["     Tècnic"]
[]
[]
["     Descripció"]

{"sheet":"2.CLIMA","index":1,"n_rows":23,"n_cols":12,"rows_kept":23,"cut":false,"hidden":false,"merged":[[0,0,0,12],[7,8,7,11]]}
["DIMENSIONAMENT INTERCANVIADOR DE TERRA - AIRE | DITA"]
[]
["2. CLIMA"]
[]
["Dades Climàtiques anuals"]
[]
[]
[]
[null,null,null,null,null,null,null,"Capitals","Barcelona"]
[]
[null,null,null,null,null,null,null,"Temp. Mitja"]
[null,null,null,null,null,null,null,"Gener",9.4,null,"Latitud"]
[null,null,null,null,null,null,null,"Febrer",9.9,null,{"$f":"(VLOOKUP($I$9,TAULES!$A$4:$AO$55,15))","v":41.24}]
[null,null,null,null,null,null,null,"Març",12.3,null,"Altitud"]
[null,null,null,null,null,null,null,"Abril",14.6,null,{"$f":"(VLOOKUP($I$9,TAULES!$A$4:$AO$55,14))","v":95}]
[null,null,null,null,null,null,null,"Maig",17.7,null,"Tmin:  Temperatura ambient mínima"]
[null,null,null,null,null,null,null,"Juny",21.6,null,{"$f":"VLOOKUP($I$9,TAULES!$A$4:$AO$55,20)","v":2},"ºC"]
[null,null,null,null,null,null,null,"Juliol",24.4,null,"Tmax:  Temperatura ambient màxima"]
[null,null,null,null,null,null,null,"Agost",24.2,null,{"$f":"VLOOKUP($I$9,TAULES!$A$4:$AO$55,19)","v":31},"ºC"]
[null,null,null,null,null,null,null,"Setembre",21.7,null,"Tm:  Temperatura mitja anual"]
[null,null,null,null,null,null,null,"Octubre",17.5,null,{"$f":"VLOOKUP($I$9,TAULES!$A$4:$AO$55,40)","v":16.416666666666664},"ºC"]
[null,null,null,null,null,null,null,"Novembre",13.5,null,"HR:  Humitat Relativa"]
[null,null,null,null,null,null,null,"Desembre",10.199999999999999,null,{"$f":"VLOOKUP($I$9,TAULES!$A$4:$AO$55,18)","v":68},"%"]

{"sheet":"3.TERRENY","index":2,"n_rows":25,"n_cols":12,"rows_kept":25,"cut":false,"hidden":false,"merged":[[0,0,0,12],[7,8,7,11],[11,8,11,11]]}
["DIMENSIONAMENT INTERCANVIADOR DE TERRA - AIRE | DITA"]
[]
["3. TERRENY"]
[]
["Selecció del tipus de terreny"]
[]
[]
[]
[]
[null,null,null,null,null,null,null,null,"Tipus Terreny:"]
[]
[null,null,null,null,null,null,null,null,"07. Llims argilosos"]
[]
[]
[]
[null,null,null,null,null,null,null,null," ce  Calor específica",null,{"$f":"+LOOKUP($I$12,PARÀMETRES!B5:B16,PARÀMETRES!C5:C16)","v":1340}," J/kgK"]
[]
[]
[null,null,null,null,null,null,null,null," λ     Conductivitat",null,{"$f":"+LOOKUP($I$12,PARÀMETRES!B5:B16,PARÀMETRES!D5:D16)","v":1.49}," W/mK"]
[]
[]
[null,null,null,null,null,null,null,null," ρ     Densitat",null,{"$f":"+LOOKUP($I$12,PARÀMETRES!B5:B16,PARÀMETRES!E5:E16)","v":1800}," kg/m3"]
[]
[]
[null,null,null,null,null,null,null,null," α     Difusivitat",null,{"$f":"(K19/K16*K22)","v":2.0014925373134331}," m2/s"]

{"sheet":"4.CONDUCTES","index":3,"n_rows":32,"n_cols":12,"rows_kept":32,"cut":false,"hidden":false,"merged":[[29,4,29,5],[31,4,31,5],[0,0,0,12],[7,8,7,11],[11,8,11,11],[25,4,25,5],[27,4,27,5]]}
["DIMENSIONAMENT INTERCANVIADOR DE TERRA - AIRE | DITA"]
[]
["4. CONDUCTE"]
[]
["Dades conducte intercanviador de calor"]
[]
[]
[]
[]
[null,null,null,null,null,null,null,null,"Tipus Conducte:"]
[]
[null,null,null,null,null,null,null,null,"01. Polipropilè"]
[]
[]
[]
[null,null,null,null,null,null,null,null," ce  Calor específica",null,{"$f":"+LOOKUP($I$12,Conducte,PARÀMETRES!C21:C26)","v":1800}," J/kgK"]
[]
[]
[null,null,null,null,null,null,null,null,"  λ    Conductivitat",null,{"$f":"+LOOKUP($I$12,Conducte,PARÀMETRES!D21:D26)","v":0.28000000000000003}," W/mK"]
[]
[]
[null,null,null,null,null,null,null,null,"  ρ    Densitat",null,{"$f":"+LOOKUP($I$12,Conducte,PARÀMETRES!E21:E26)","v":990}," kg/m³"]
[]
[]
[]
[null,null,"z","  Profunditat",2,null,"  m"]
[]
[null,null,"L","  Longitud ",30,null,"  m"]
[]
[null,null,"Øi","  Diàmetre",0.4,null,"  m"]
[]
[null,null,"e","  Gruix",{"$f":"1.5/100","v":1.4999999999999999E-2},null,"  m"]

{"sheet":"5.CÀLCUL","index":4,"n_rows":30,"n_cols":14,"rows_kept":30,"cut":false,"hidden":false,"merged":[[31,4,31,7],[0,0,0,14],[25,4,25,5],[29,4,29,7],[23,4,23,7],[27,4,27,5]]}
["DIMENSIONAMENT INTERCANVIADOR DE TERRA - AIRE | DITA"]
[]
["5. CÀLCUL"]
[]
[]
[]
[]
[null,null,null,null,null,null,null,null,null,"Te","Temperatura entrada",null,31,"  ºC"]
[]
[null,null,null,null,null,null,null,null,null,"Ta","Temperatura ambient anual",null,{"$f":"'2.CLIMA'!K21+('2.CLIMA'!K19-'2.CLIMA'!K21)*COS((2*PI()*((365*3600)/PARÀMETRES!D38)))","v":30.50308496671558},"  ºC"]
[]
[null,null,null,null,null,null,null,null,null,"Tg","Temperatura terreny anual",null,{"$f":"GRÀFICA!F20","v":16.416666666666668},"  ºC"]
[]
[null,null,null,null,null,null,null,null,null,"Tg (z)","Temp. terreny a profunditat z",null,{"$f":"('2.CLIMA'!K21+(M8-'2.CLIMA'!K21)*EXP(-('4.CONDUCTES'!E26/PARÀMETRES!D41))*COS((2*PI()*(1/PARÀMETRES!D38))-('4.CONDUCTES'!E26/PARÀMETRES!D41)))","v":20.952838114295069},"  ºC"]
[]
[]
[null,null,null,null,null,null,null,null,null,null," Rcd","Resistència Conducció",{"$f":"LN(('4.CONDUCTES'!E30+(2*'4.CONDUCTES'!E32))/'4.CONDUCTES'!E30)*('4.CONDUCTES'!E30+'4.CONDUCTES'!E32+'4.CONDUCTES'!E32)/(2*'4.CONDUCTES'!K19)","v":5.5531936570070023E-2}," m²K/W"]
[]
[null,null,null,null,null,null,null,null,null,null," Rcv","Resistència Convecció",{"$f":"('4.CONDUCTES'!E30)/(PARÀMETRES!D36*PARÀMETRES!D32)","v":0.24974595960764903}," m²K/W"]
[]
[null,null,null,null,null,null,null,null,null,null," Rg","Resistència Terreny",{"$f":"(LN(('4.CONDUCTES'!E30+2*('4.CONDUCTES'!E32+PARÀMETRES!D40))/('4.CONDUCTES'!E30+(2*'4.CONDUCTES'!E32)))*('4.CONDUCTES'!E30+'4.CONDUCTES'!E32+'4.CONDUCTES'!E32))/(2*'3.TERRENY'!K19)","v":6.8381395329273092E-2}," m²K/W"]
[]
[null,null,null,null,null,null,null,null,null,null," Ut","Transmitància Total",{"$f":"1/(M17+M19+M21)","v":2.6762348019419915}," W/m²K"]
[null,null,"V"," Volum",1200,null,null,null,"  m³"]
[]
[null,null,"ra"," Renovacions",1,null,"Persones ",5,"  pers"]
[]
[null,null,"Qv"," Cabal","01. Local",null,null,{"$f":"+LOOKUP($E$28,PARÀMETRES!B47:D51,PARÀMETRES!D47:D51)","v":1200},"  m³/h",null," Ts","Temperatura sortida",{"$f":"M14-(M14-M8)*EXP(-((3600*M23*PI()*'4.CONDUCTES'!E30*'4.CONDUCTES'!E28)/(PARÀMETRES!D30*PARÀMETRES!D31*'5.CÀLCUL'!H28)))","v":28.773853089778196},"ºC"]
[]
[null,null,"v"," Velocitat",1,null,null,null,"  m/s"]

{"sheet":"PARÀMETRES","index":5,"n_rows":51,"n_cols":5,"rows_kept":51,"cut":false,"hidden":true,"merged":[[2,0,2,4],[18,0,18,4],[28,0,28,4],[44,0,44,4]]}
[]
[]
["TERRENY"]
[null,"Terreny","Calor Específica\n(J/KgK)","Conductivitat\n(W/mk)","Densitat\n(kg/m3)"]
[null,"01. Calcària",2230,0.71,1670]
[null,"02. Sorra",1390,0.93,1780]
[null,"03. Sorra seca",920,0.7,1500]
[null,"04. Terreny sorrenc",1650,1.24,1520]
[null,"05. Gres",710,1.87,2250]
[null,"06. Argila",880,1.28,1500]
[null,"07. Llims argilosos",1340,1.49,1800]
[null,"08. Terreny argilenc",2850,2.2999999999999998,1650]
[null,"09. Terreny argilenc humit",1340,1.4,1800]
[null,"10. Grava seca",909,0.5,1650]
[null,"11. Terreny sec",840,0.87,2022]
[null,"12. Terra lleugerament seca",840,0.35,1442]
[]
[]
["CONDUCTE"]
[null,"Material conducte","Calor Específica\n(J/KgK)","Conductivitat\n(W/mk)","Densitat\n(kg/m3)"]
[null,"01. Polipropilè",1800,0.28000000000000003,990]
[null,"02. Polietilè TPC",1800,0.5,980]
[null,"03. Gres vitrificat",1000,1.04,2400]
[null,"04. PVC",1024,0.16,1379]
[null,"05. Formigó",1000,2,2500]
[null,"06. Ferro",550,40,7100]
[]
[]
["PARAMETRES"]
[null,"ρa:","Densitat aire",1.2,"kg/m3"]
[null,"ce:","Calor específica aire",1007,"J/kgK"]
[null,"λa:","Conductivitat aire",2.5999999999999999E-2,"W/mk"]
[null,"mu:","Resistència fregament",1.8479999999999999E-5]
[null,"Pr:","Núm. Prand",0.71]
[null,"Re:","Núm. Reynolds",{"$f":"('5.CÀLCUL'!E30*'4.CONDUCTES'!E30*D30)/(D33)","v":25974.025974025975}]
[null,"Nu:","Núm. Nusselt",{"$f":"IF(D35<3000,3.66,0.0214*((D35^0.8)-100)*(D34^0.4))","v":61.601058166404862}]
[null,"t:","Temps ús anual",{"$f":"3600*365*5","v":6570000},"s"]
[null,"to:","1 any",{"$f":"365*24*60*60","v":31536000},"s"]
[null,"ξ:","Profunditat tèrmica tub",{"$f":"'4.CONDUCTES'!E26/'3.TERRENY'!K25","v":0.99925428784489168}]
[null,"ɗ:","Profunditat penetració",{"$f":"SQRT(('3.TERRENY'!K19*24*3600)/(PI()*'3.TERRENY'!K22*'3.TERRENY'!K16))","v":0.13034261127249167},"m (diària)"]
[null,"ɗ:","Profunditat penetració",{"$f":"SQRT((PARÀMETRES!D38*'3.TERRENY'!K19)/('3.TERRENY'!K16*'3.TERRENY'!K22*PI()))","v":2.4901920918608136},"m (anual)"]
[]
[]
[]
["CABALS"]
[null,"Tipus","Cabal unitari","Cabal total"]
[null,"01. Local",{"$f":"'5.CÀLCUL'!$E$24*'5.CÀLCUL'!$E$26","v":1200},{"$f":"C47","v":1200}]
[null,"02. IDA 1",{"$f":"20*3.6","v":72},{"$f":"C48*'5.CÀLCUL'!$H$26","v":360}]
[null,"03. IDA 2",{"$f":"12.5*3.6","v":45},{"$f":"C49*'5.CÀLCUL'!$H$26","v":225}]
[null,"04. IDA 3",{"$f":"8*3.6","v":28.8},{"$f":"C50*'5.CÀLCUL'!$H$26","v":144}]
[null,"05. IDA 4",{"$f":"5*3.6","v":18},{"$f":"C51*'5.CÀLCUL'!$H$26","v":90}]

{"sheet":"TAULES","index":6,"n_rows":292,"n_cols":69,"rows_kept":292,"cut":false,"hidden":true,"merged":[[1,1,1,12],[1,20,1,31],[55,0,55,12],[1,55,1,66]]}
["1","2","3","4","5","6","7","8","9","10","11","12","13","14","15","16","17","18","19","20","21","22","23","24","25","26","27","28","29","30","31","32","33","34","35","36","37","38","39","40","41","42","43","44","45","46","47","48","49","50","51","52","53","54","55","56","57","58","59","60","61","62","63","64","65","66","67","68","69"]
[null,"RADIACIÓ HORIZONTAL                                                                                                                                                                                                                                                                                                                                                                                            [kJ/m2/día]",null,null,null,null,null,null,null,null,null,null,null,"ALTITUD             [m]","LATITUD                     [ º , ' ]","LATITUD             [ º ]","VARIACIÓ DIURNA [ºC]","HUMITAT RELATIVA [%]","TEMPERATURA MÀXIMA ESTIU [ºC]","TEMPERATURA MÍNIMA HIVERN [ºC]","TEMPERATURA AMBIENT  (durant las hores de sol )                                                                                                                                                                                                                                                                                                                                                                                                   [ºC]",null,null,null,null,null,null,null,null,null,null,null,"GRAUS DIA NOV./MAR.","GRAUS DIA ANUAL","DIRECCIÓ DEL VENT","VELOCITAT DEL VENT [m/s]","TEMPERATURA AIGUA XARXA [ºC]","TEMPERATURA AMB. MÍNIMA HISTÒRICA [ºC]",null,"TEMPERATURA AMB. MITJA ANUAL [ºC]","ZONA CLIMÁTICA",null,null,null,null,null,null,null,null,null,null,null,null,null,null,"RADIACIÓN HORIZONTAL                                                                                                                                                                                                                                                                                                                                                                                            [Wh/m2/día]",null,null,null,null,null,null,null,null,null,null,null,null,"FUENTE (Datos de Radiación Horizontal)"]
[null,"Gener","Febrer","Març","Abril","Maig","Juny","Juliol","Agost","Setembre","Octubre","Novembre","Desembre",null,null,null,null,null,null,null,"Gener","Febrer","Març","Abril","Maig","Juny","Juliol","Agost","Setembre","Octubre","Novembre","Desembre",null,null,null,null,null,null,null,null,null,"Provincia","ENE","FEB","MAR","ABR","MAY","JUN","JUL","AGO","SEP","OCT","NOV","DIC","AÑO","Enero","Febrero","Marzo","Abril","Mayo","Junio","Julio","Agosto","Septiembre","Octubre","Noviembre","Diciembre"]
["Albacete",6700,10500,15000,19200,21200,25100,26700,23200,18800,12400,8400,6400,686,39,39,18,36,35,-7,4.2,5.6,9,11,15.3,21.6,24.1,23.8,17.8,13.7,8.6999999999999993,5.2,1247.5999999999999,1377.4,"O",12,10,-23,"Albacete",{"$f":"(SUM(U4:AF4))/12","v":13.33333333333333},"D","ÁLAVA",7,7,11,12,15,19,21,21,19,15,10,7,"13.7",{"$f":"B4/3.6","v":1861.1111111111111},{"$f":"C4/3.6","v":2916.6666666666665},{"$f":"D4/3.6","v":4166.666666666667},{"$f":"E4/3.6","v":5333.333333333333},{"$f":"F4/3.6","v":5888.8888888888887},{"$f":"G4/3.6","v":6972.2222222222217},{"$f":"H4/3.6","v":7416.6666666666661},{"$f":"I4/3.6","v":6444.4444444444443},{"$f":"J4/3.6","v":5222.2222222222217},{"$f":"K4/3.6","v":3444.4444444444443},{"$f":"L4/3.6","v":2333.3333333333335},{"$f":"M4/3.6","v":1777.7777777777778},{"$f":"AJ4*1000/3600","v":3.3333333333333335},"Centro de Estudios de la Energía (Ministerio de Industria y Energía) "]
["Alicante",8500,12000,16300,18900,23100,24800,25800,22500,18300,13600,9800,7600,7,38.21,38.35,13,60,31,2,11,11.8,14,15.9,19,22.8,25.5,26.1,23.7,19.3,15.2,12,338.2,338.2,"SE",9,10,-5,"Alicante",{"$f":"(SUM(U5:AF5))/12","v":18.024999999999999},"A","ALBACETE",6,8,11,13,17,22,26,26,22,16,11,7,"15.4",2361.1111111111109,3333.333333333333,4527.7777777777774,5250,6416.6666666666661,6888.8888888888887,7166.6666666666661,6250,5083.333333333333,3777.7777777777778,2722.2222222222222,2111.1111111111109,2.5,"Centro de Estudios de la Energía (Ministerio de Industria y Energía) "]
["Almería",8900,12200,16400,19600,23100,24600,25300,22500,18500,13900,10000,8000,65,36.51,36.85,8,70,30,5,11.7,11.8,14.1,16.100000000000001,18.399999999999999,22,24.7,25.3,23.4,19.399999999999999,15.6,12.8,207.9,207.9,"OSO",9,12,-1,"Almería",17.941666666666666,"A","ALICANTE",13,14,16,18,21,25,28,28,26,21,17,14,"20.1",2472.2222222222222,3388.8888888888887,4555.5555555555557,5444.4444444444443,6416.6666666666661,6833.333333333333,7027.7777777777774,6250,5138.8888888888887,3861.1111111111109,2777.7777777777778,2222.2222222222222,2.5,"Centro de Estudios de la Energía (Ministerio de Industria y Energía) "]
["Ávila",6000,9100,13500,17700,19400,22300,26300,25300,18800,11200,6900,5200,1126,40.39,40.65,17,41,30,-6,2.4,3.3,6.3,8.6999999999999993,12.2,16.399999999999999,20,19.8,16.3,10.6,6,3.2,1672.6,2127.1999999999998,"NO",11,10,-21,"Avila",10.433333333333332,"E","ALMERÍA",15,15,16,18,21,24,27,28,26,22,18,16,"20.5",1666.6666666666665,2527.7777777777778,3750,4916.666666666667,5388.8888888888887,6194.4444444444443,7305.5555555555557,7027.7777777777774,5222.2222222222217,3111.1111111111109,1916.6666666666665,1444.4444444444443,3.0555555555555554,"Centro de Estudios de la Energía (Ministerio de Industria y Energía) "]
["Badajoz",6500,10000,13600,18700,21800,24600,25900,23800,17900,12300,8200,6200,186,38.53,38.880000000000003,17,47,38,-1,8.6,9.9,12.7,15.2,18,22.8,25.8,25.5,22.6,17.8,12.6,9.1,749.4,767.4,"NO",7,10,-6,"Badajoz",16.716666666666665,"B","ASTURIAS",9,10,11,12,15,18,20,20,19,16,12,10,"14.3",1805.5555555555554,2777.7777777777778,3777.7777777777778,5194.4444444444443,6055.5555555555557,6833.333333333333,7194.4444444444443,6611.1111111111113,4972.2222222222217,3416.6666666666665,2277.7777777777778,1722.2222222222222,1.9444444444444444,"Centro de Estudios de la Energía (Ministerio de Industria y Energía) "]
["Baleares",7200,10700,14400,16200,21000,22700,24200,20600,16400,12100,8500,6500,28,39.340000000000003,39.57,8,63,28,4,10.5,10.5,12.2,14.5,17.399999999999999,21.4,24.1,24.5,22.6,18.399999999999999,14.3,11.6,503.4,527.4,"VARIA",9,11,-4,"Baleares",16.833333333333332,"B","ÁVILA",4,5,8,11,14,18,22,22,18,13,8,5,"12.3",2000,2972.2222222222222,4000,4500,5833.333333333333,6305.5555555555557,6722.2222222222217,5722.2222222222217,4555.5555555555557,3361.1111111111109,2361.1111111111109,1805.5555555555554,2.5,"Centro de Estudios de la Energía (Ministerio de Industria y Energía) "]
["Barcelona",6700,9300,13400,17900,21500,23400,22900,20100,16000,11500,7900,6100,95,41.24,41.4,8,68,31,2,9.4,9.9,12.3,14.6,17.7,21.6,24.4,24.2,21.7,17.5,13.5,10.199999999999999,622.70000000000005,655.7,"S",8,12,-20,"Barcelona",16.416666666666664,"B","BADAJOZ",11,12,15,17,20,25,28,28,25,20,15,11,"18.9",1861.1111111111111,2583.3333333333335,3722.2222222222222,4972.2222222222217,5972.2222222222217,6500,6361.1111111111113,5583.333333333333,4444.4444444444443,3194.4444444444443,2194.4444444444443,1694.4444444444443,2.2222222222222223,"Institut Català d'Energia. Atlas de radiaciò solar a Catalunya. Ediciò 1996"]
["Burgos",5100,7900,12400,16000,18700,21500,23000,20700,16700,10100,6500,4500,929,42.2,42.33,15,42,30,-6,2.5,4.8,7.1,9.1999999999999993,12.2,16.2,19,18.8,16.2,11.3,6.5,3.4,1615.2,2048.4,"SO",8,9,-18,"Burgos",10.6,"E","BALEARES",12,13,14,17,19,23,26,27,25,20,16,14,"18.8",1416.6666666666667,2194.4444444444443,3444.4444444444443,4444.4444444444443,5194.4444444444443,5972.2222222222217,6388.8888888888887,5750,4638.8888888888887,2805.5555555555557,1805.5555555555554,1250,2.2222222222222223,"Centro de Estudios de la Energía (Ministerio de Industria y Energía) "]
["Cáceres",6800,10000,14700,19600,22100,25100,28100,25400,19700,12700,8900,6600,459,39.29,39.479999999999997,14,37,38,-1,7.7,9.1,11.7,14.4,17.399999999999999,22.5,26,25.6,22.3,16.899999999999999,11.7,8.1,946.1,1003.1,"NO",7,11,-6,"Caceres",16.116666666666667,"C","BARCELONA",11,12,14,17,20,24,26,26,24,20,16,12,"18.5",1888.8888888888889,2777.7777777777778,4083.333333333333,5444.4444444444443,6138.8888888888887,6972.2222222222217,7805.5555555555557,7055.5555555555557,5472.2222222222217,3527.7777777777778,2472.2222222222222,1833.3333333333333,1.9444444444444444,"Centro de Estudios de la Energía (Ministerio de Industria y Energía) "]
["Cádiz",8100,11500,15700,18500,22200,23800,25900,23000,18100,14200,10000,7400,28,36.28,36.47,12,55,32,2,11.4,12.5,14.6,16.600000000000001,18.899999999999999,22.2,24.5,24.9,23.4,19.5,15.6,12.5,227.4,227.4,"SE",20,10,-2,"Cádiz",18.05,"A","BURGOS",5,6,9,11,14,18,21,21,18,13,9,5,"12.5",2250,3194.4444444444443,4361.1111111111113,5138.8888888888887,6166.6666666666661,6611.1111111111113,7194.4444444444443,6388.8888888888887,5027.7777777777774,3944.4444444444443,2777.7777777777778,2055.5555555555557,5.5555555555555554,"Centro de Estudios de la Energía (Ministerio de Industria y Energía) "]
["Canarias",9766,11700,14880,17602,17844,15932,15358,14990,16624,12160,9650,7370,6,28.11,28.18,4,66,24,15,18.3,19.600000000000001,19.100000000000001,19.600000000000001,20.3,21.4,23.8,23.6,25.9,23.3,22.1,19.899999999999999,241.1,259.10000000000002,"NE",9,10,3,"Canarias",21.408333333333335,"A","CÁCERES",10,11,14,16,19,25,28,28,25,19,14,10,"18.3",2712.7777777777778,3250,4133.333333333333,4889.4444444444443,4956.666666666667,4425.5555555555557,4266.1111111111113,4163.8888888888887,4617.7777777777774,3377.7777777777778,2680.5555555555557,2047.2222222222222,2.5,"Centro de Estudios de la Energía (Ministerio de Industria y Energía) "]
["Castellón",8000,12200,15500,17400,20600,21400,23900,19500,16600,13100,8600,7300,27,39.590000000000003,39.979999999999997,9,60,29,4,10.4,11.1,13.1,14.9,17.8,21.6,24.3,24.7,22.6,18.600000000000001,14.3,11.1,443.4,452.4,"NO",3,10,-8,"Castellón",17.041666666666668,"B","CÁDIZ",13,15,17,19,21,24,27,27,25,22,18,15,"20.3",2222.2222222222222,3388.8888888888887,4305.5555555555557,4833.333333333333,5722.2222222222217,5944.4444444444443,6638.8888888888887,5416.666666666667,4611.1111111111113,3638.8888888888887,2388.8888888888887,2027.7777777777778,0.83333333333333337,"Centro de Estudios de la Energía (Ministerio de Industria y Energía) "]
["Ciudad Real",7000,10100,15000,18700,21400,23700,25300,23200,18800,12500,8700,6500,628,38.590000000000003,38.979999999999997,20,56,37,-4,5.4,7.3,10.4,12.9,16.3,21.2,25.5,24.8,21,14.8,8.9,6.2,1201.2,1312.6,"SO",4,10,-10,"Ciudad Real",14.558333333333335,"D","CANTABRIA",11,11,14,14,16,19,21,21,20,17,14,12,"15.8",1944.4444444444443,2805.5555555555557,4166.666666666667,5194.4444444444443,5944.4444444444443,6583.333333333333,7027.7777777777774,6444.4444444444443,5222.2222222222217,3472.2222222222222,2416.6666666666665,1805.5555555555554,1.1111111111111112,"Centro de Estudios de la Energía (Ministerio de Industria y Energía) "]
["Córdoba",7200,10100,15100,18500,21800,25900,28500,25100,19900,12600,8600,6900,128,37.53,37.880000000000003,17,33,38,-1,9.1,10.7,13.5,16.3,19.399999999999999,24.4,27.9,27.6,24.3,18.600000000000001,13.6,9.6,653.70000000000005,662.7,"SO",5,10,-6,"Córdoba",17.916666666666668,"B","CASTELLÓN",13,13,15,17,20,24,26,27,25,21,16,13,"19.2",2000,2805.5555555555557,4194.4444444444443,5138.8888888888887,6055.5555555555557,7194.4444444444443,7916.6666666666661,6972.2222222222217,5527.7777777777774,3500,2388.8888888888887,1916.6666666666665,1.3888888888888888,"Centro de Estudios de la Energía (Ministerio de Industria y Energía) "]
["Cuenca",5900,8800,12900,17400,18700,22000,25600,22300,17500,11200,7200,5500,949,40.049999999999997,40.08,18,52,33,-7,3.1,4.2,7.3,10,13.3,18.100000000000001,21.9,21.4,18,12,7.2,4.0999999999999996,1520.8,1828,"O",8,9,-21,"Cuenca",11.716666666666667,"E","CEUTA",15,15,16,17,19,23,25,26,24,21,18,16,"19.6",1638.8888888888889,2444.4444444444443,3583.333333333333,4833.333333333333,5194.4444444444443,6111.1111111111113,7111.1111111111113,6194.4444444444443,4861.1111111111113,3111.1111111111109,2000,1527.7777777777778,2.2222222222222223,"Centro de Estudios de la Energía (Ministerio de Industria y Energía) "]
["Gerona",7238,10204,13624,17300,20600,22200,21700,19000,15000,10900,7500,6000,95,41.59,41.98,10,58,33,-3,7.1,8.4,11.1,13.4,16.8,20.7,23.5,23.3,20.9,16,11.3,8,873.3,939.3,"S",5,11,-11,"Gerona",15.041666666666666,"C","CIUDAD REAL",7,9,12,15,18,23,28,27,20,17,11,8,"16.3",2010.5555555555554,2834.4444444444443,3784.4444444444443,4805.5555555555557,5722.2222222222217,6166.6666666666661,6027.7777777777774,5277.7777777777774,4166.666666666667,3027.7777777777778,2083.3333333333335,1666.6666666666665,1.3888888888888888,"Centro de Estudios de la Energía (Ministerio de Industria y Energía) "]
["Granada",7800,10800,15200,18500,21900,24800,26700,23600,18800,12900,9600,7100,775,37.11,37.18,18,49,36,-2,7,8.4,11,13.3,16.3,21.8,25.7,25.3,21.8,16,11.6,7.7,972.8,1041.8,"O",4,11,-13,"Granada",15.491666666666667,"C","CÓRDOBA",11,13,16,18,21,26,30,30,26,21,16,12,20,2166.6666666666665,3000,4222.2222222222217,5138.8888888888887,6083.333333333333,6888.8888888888887,7416.6666666666661,6555.5555555555557,5222.2222222222217,3583.333333333333,2666.6666666666665,1972.2222222222222,1.1111111111111112,"Centro de Estudios de la Energía (Ministerio de Industria y Energía) "]
["Guadalajara",6500,9200,14000,17900,19400,22700,25000,23200,17800,11700,7800,5600,1017,40.380000000000003,40.630000000000003,15,37,34,-4,3.5,5.9,9.5,11.9,15.6,20.2,24.3,23.5,19.8,13.7,8.4,5.5,1287,1468.6,"O",10,10,-14,"Guadalajara",13.483333333333333,"D","CUENCA",5,6,9,12,15,20,24,23,20,14,9,6,"13.6",1805.5555555555554,2555.5555555555557,3888.8888888888887,4972.2222222222217,5388.8888888888887,6305.5555555555557,6944.4444444444443,6444.4444444444443,4944.4444444444443,3250,2166.6666666666665,1555.5555555555554,2.7777777777777777,"Centro de Estudios de la Energía (Ministerio de Industria y Energía) "]
["Guipúzcoa",5500,7700,11300,11700,14600,16200,16100,13600,12700,10300,6200,5000,181,43.19,43.32,7,76,22,-1,7.8,7.7,10.7,11.8,10.5,16.8,15.1,19,18.100000000000001,14.7,10.7,8,807.9,913.1,"S",17,12,-12,"Guipuzcoa",12.574999999999998,"C","GERONA",9,10,13,15,19,23,26,25,23,18,13,10,17,1527.7777777777778,2138.8888888888887,3138.8888888888887,3250,4055.5555555555557,4500,4472.2222222222217,3777.7777777777778,3527.7777777777778,2861.1111111111109,1722.2222222222222,1388.8888888888889,4.7222222222222223,"Centro de Estudios de la Energía (Ministerio de Industria y Energía) "]
["Huelva",7600,11300,16000,19500,24100,25600,28700,25600,21200,14500,9200,7500,4,37.159999999999997,37.270000000000003,14,57,31,1,11.1,12.3,14.4,18.399999999999999,18.899999999999999,22.4,25,25.2,23.3,19.399999999999999,15.2,11.9,402.3,402.3,"SO",1,10,-6,"Huelva",18.125,"B","GRANADA",9,10,13,16,18,24,27,27,24,18,13,9,"17.3",2111.1111111111109,3138.8888888888887,4444.4444444444443,5416.666666666667,6694.4444444444443,7111.1111111111113,7972.2222222222217,7111.1111111111113,5888.8888888888887,4027.7777777777778,2555.5555555555557,2083.3333333333335,0.27777777777777779,"Centro de Estudios de la Energía (Ministerio de Industria y Energía) "]
["Huesca",6100,9600,14300,18700,20300,22100,23100,20900,16900,11300,7200,5100,488,42.08,42.13,15,72,31,-5,4.5999999999999996,6.1,10.199999999999999,12.5,15.9,19.899999999999999,22.8,22.5,19.3,14,8.9,5.4,1232.5,1350.1,"SO",1,10,-14,"Huesca",13.508333333333333,"D","GUADALAJARA",7,8,12,14,18,22,26,26,22,16,10,8,"15.8",1694.4444444444443,2666.6666666666665,3972.2222222222222,5194.4444444444443,5638.8888888888887,6138.8888888888887,6416.6666666666661,5805.5555555555557,4694.4444444444443,3138.8888888888887,2000,1416.6666666666667,0.27777777777777779,"Centro de Estudios de la Energía (Ministerio de Industria y Energía) "]
["Jaén",6700,10100,14400,18000,20300,24400,26700,24100,19200,11900,8100,6500,586,37.46,37.770000000000003,14,35,36,0,8.1999999999999993,9.6,12.3,14.1,18.3,23.8,27.7,27.3,23.4,17.600000000000001,12.7,8.9,791.4,830.4,"SO",5,11,-8,"Jaen",16.991666666666667,"C","GUIPÚZCOA",10,10,13,14,16,19,21,21,20,17,13,10,"15.3",1861.1111111111111,2805.5555555555557,4000,5000,5638.8888888888887,6777.7777777777774,7416.6666666666661,6694.4444444444443,5333.333333333333,3305.5555555555557,2250,1805.5555555555554,1.3888888888888888,"Centro de Estudios de la Energía (Ministerio de Industria y Energía) "]
["La Coruña",5400,8000,11400,12400,15400,16200,17400,15300,13900,10900,6400,5100,54,43.22,43.37,9,63,23,2,9.9,9.8000000000000007,11.5,12.4,14,16.5,18.2,18.899999999999999,17.8,15.3,12.4,10.199999999999999,688.2,827.5,"SO",18,10,-9,"La Coruña",13.908333333333333,"C","HUELVA",13,14,16,20,21,24,27,27,25,21,17,14,"19.9",1500,2222.2222222222222,3166.6666666666665,3444.4444444444443,4277.7777777777774,4500,4833.333333333333,4250,3861.1111111111109,3027.7777777777778,1777.7777777777778,1416.6666666666667,5,"Centro de Estudios de la Energía (Ministerio de Industria y Energía) "]
["León",5800,8700,13800,17200,19500,22100,24200,20900,17200,10400,7000,4800,908,42.35,42.58,16,45,28,-6,2.8,4.2,7.6,9.9,12.5,17.2,19.7,19.5,16.600000000000001,11.8,7,3.6,1693.7,2142.6,"NO",8,9,-18,"León",11.033333333333333,"E","HUESCA",7,8,12,15,18,22,25,25,21,16,11,7,"15.6",1611.1111111111111,2416.6666666666665,3833.333333333333,4777.7777777777774,5416.666666666667,6138.8888888888887,6722.2222222222217,5805.5555555555557,4777.7777777777774,2888.8888888888887,1944.4444444444443,1333.3333333333333,2.2222222222222223,"Centro de Estudios de la Energía (Ministerio de Industria y Energía) "]
["Lérida",6078,12168,15592,19226,21954,24900,24638,21340,16740,11980,6302,4006,323,41.41,41.68,14,50,33,-5,4.9000000000000004,9.5,11.3,11.9,16.100000000000001,19.600000000000001,24.1,24.4,21.9,14.9,8.3000000000000007,7.3,1189.7,1225.7,"S",1,7,-11,"Lérida",14.516666666666671,"C","JAÉN",11,11,14,17,21,26,30,29,25,19,15,10,19,1688.3333333333333,3380,4331.1111111111113,5340.5555555555557,6098.333333333333,6916.6666666666661,6843.8888888888887,5927.7777777777774,4650,3327.7777777777778,1750.5555555555554,1112.7777777777778,0.27777777777777779,"Centro de Estudios de la Energía (Ministerio de Industria y Energía) "]
["Logroño",5986,9630,13606,18254,21228,23572,25224,21396,16538,11808,6740,5024,380,42.28,42.47,14,59,33,-3,5.0999999999999996,6.5,9.6999999999999993,11.9,14.9,19.100000000000001,21.8,21.5,19,13.8,8.9,{"$f":"6+0.1","v":6.1},1229.4000000000001,1404.9,"NO",15,10,-12,"Logroño",13.191666666666668,"D","LA CORUÑA",12,12,14,14,16,19,20,21,20,17,14,12,"15.9",1662.7777777777778,2675,3779.4444444444443,5070.5555555555557,5896.666666666667,6547.7777777777774,7006.6666666666661,5943.333333333333,4593.8888888888887,3280,1872.2222222222222,1395.5555555555554,4.166666666666667,"Centro de Estudios de la Energía (Ministerio de Industria y Energía) "]
["Lugo",5100,7600,11700,15200,17100,19500,20200,18400,15000,9900,6200,4500,465,43,43,14,67,26,-2,6,6.9,9.4,11,13.1,16.3,18.100000000000001,16.600000000000001,16.8,13.2,8.8000000000000007,6.2,1377.8,1770.9,"NE",12,11,-8,"Lugo",11.866666666666667,"D","LA RIOJA",7,9,12,14,17,21,24,24,21,16,11,8,"15.3",1416.6666666666667,2111.1111111111109,3250,4222.2222222222217,4750,5416.666666666667,5611.1111111111113,5111.1111111111113,4166.666666666667,2750,1722.2222222222222,1250,3.3333333333333335,"Centro de Estudios de la Energía (Ministerio de Industria y Energía) "]
["Madrid",6700,10600,13600,18800,20900,23500,26000,23100,16900,11400,7500,5900,667,40.25,40.42,15,42,34,-3,4.9000000000000004,6.5,10,13,15.7,20.6,24.2,23.6,19.8,14,8.9,5.6,1259.5,1404.9,"NE",10,10,-16,"Madrid",13.9,"D","LAS PALMAS",20,20,21,22,23,24,25,25,26,25,23,21,"22.9",1861.1111111111111,2944.4444444444443,3777.7777777777778,5222.2222222222217,5805.5555555555557,6527.7777777777774,7222.2222222222217,6416.6666666666661,4694.4444444444443,3166.6666666666665,2083.3333333333335,1638.8888888888889,2.7777777777777777,"Centro de Estudios de la Energía (Ministerio de Industria y Energía) "]
["Málaga",8300,12000,15500,18500,23200,24500,26500,23200,19000,13600,9300,8000,40,36.43,36.72,6,60,28,13,12.5,12.9,15,16.3,19.3,22.8,25.2,25.6,23.5,19.7,15.8,13.3,247.6,247.6,"S",7,12,-4,"Málaga",18.491666666666667,"A","LEÓN",5,6,10,12,15,19,22,22,19,14,9,6,"13.3",2305.5555555555557,3333.333333333333,4305.5555555555557,5138.8888888888887,6444.4444444444443,6805.5555555555557,7361.1111111111113,6444.4444444444443,5277.7777777777774,3777.7777777777778,2583.3333333333335,2222.2222222222222,1.9444444444444444,"Centro de Estudios de la Energía (Ministerio de Industria y Energía) "]
["Melilla",9400,12600,17200,20300,23000,24800,24800,22600,18300,14200,10900,8700,40,36.43,36.72,null,null,null,null,12.5,12.9,15,16.3,19.3,22.8,25.2,25.6,23.5,19.7,15.8,13.3,225,225,"S",7,10,-1,"Melilla",18.491666666666667,"A","LÉRIDA",7,10,14,15,21,24,27,27,23,18,11,8,"17.1",2611.1111111111109,3500,4777.7777777777774,5638.8888888888887,6388.8888888888887,6888.8888888888887,6888.8888888888887,6277.7777777777774,5083.333333333333,3944.4444444444443,3027.7777777777778,2416.6666666666665,1.9444444444444444,"Centro de Estudios de la Energía (Ministerio de Industria y Energía) "]
["Murcia",10100,14800,16600,20400,24200,25600,27700,23500,18600,13900,9800,8100,42,37.590000000000003,37.979999999999997,14,59,36,-1,10.7,11.6,14.2,16,19.5,23.4,26,26.3,23.8,18.899999999999999,14.4,11.6,432.5,432.5,"SO",1,10,-5,"Murcia",18.033333333333335,"B","LUGO",8,9,11,13,15,18,20,21,19,15,11,8,14,2805.5555555555557,4111.1111111111113,4611.1111111111113,5666.666666666667,6722.2222222222217,7111.1111111111113,7694.4444444444443,6527.7777777777774,5166.666666666667,3861.1111111111109,2722.2222222222222,2250,0.27777777777777779,"Centro de Estudios de la Energía (Ministerio de Industria y Energía) "]
["Orense",4700,7300,11300,14000,16200,17600,18300,16600,14300,9400,5600,4300," ",42.3,null,9,55,33,-3,6.6,7.2,10.7,12.6,16.100000000000001,19.100000000000001,21.8,21.2,18.7,13.9,9.5,7.3,910.4,967.4,"SO",18,11,-8,"Orense",13.725000000000001,"C","MADRID",6,8,11,13,18,23,28,26,21,15,11,7,"15.6",1305.5555555555554,2027.7777777777778,3138.8888888888887,3888.8888888888887,4500,4888.8888888888887,5083.333333333333,4611.1111111111113,3972.2222222222222,2611.1111111111109,1555.5555555555554,1194.4444444444443,5,"Centro de Estudios de la Energía (Ministerio de Industria y Energía) "]
["Oviedo",5360,7536,10426,12892,15280,16622,16204,14196,12100,8040,5610,4272,232,43.22,43.37,9,70,26,-2,9.3000000000000007,9.4,11.3,12.3,14.1,17,19.600000000000001,19.5,18.100000000000001,15.1,12,10.1,978.6,1200.3,"NE",1,10,-11,"Oviedo",13.983333333333333,"C","MÁLAGA",15,15,17,19,21,25,27,28,26,22,18,15,"20.7",{"$f":"B36/3.6","v":1488.8888888888889},{"$f":"C36/3.6","v":2093.3333333333335},{"$f":"D36/3.6","v":2896.1111111111109},{"$f":"E36/3.6","v":3581.1111111111109},{"$f":"F36/3.6","v":4244.4444444444443},{"$f":"G36/3.6","v":4617.2222222222217},{"$f":"H36/3.6","v":4501.1111111111113},{"$f":"I36/3.6","v":3943.333333333333},{"$f":"J36/3.6","v":3361.1111111111109},{"$f":"K36/3.6","v":2233.3333333333335},{"$f":"L36/3.6","v":1558.3333333333333},{"$f":"M36/3.6","v":1186.6666666666667},{"$f":"AJ36*1000/3600","v":0.27777777777777779},"Centro de Estudios de la Energía (Ministerio de Industria y Energía) "]
["Palencia",5300,9000,13200,17500,19700,21800,24100,21600,17100,10900,6600,4600,734,42,42,16,45,30,-6,3.3,4.5999999999999996,8.1999999999999993,10.5,13.5,18.100000000000001,21,20.8,17.600000000000001,12.2,7.2,3.9,1483.4,1781.5,"NE",1,10,-14,"Palencia",11.741666666666665,"D","MELILLA",15,15,16,18,21,25,27,28,26,22,18,16,"20.6",1472.2222222222222,2500,3666.6666666666665,4861.1111111111113,5472.2222222222217,6055.5555555555557,6694.4444444444443,6000,4750,3027.7777777777778,1833.3333333333333,1277.7777777777778,0.27777777777777779,"Centro de Estudios de la Energía (Ministerio de Industria y Energía) "]
["Pamplona",4722.9677419354839,8812.2857142857138,15305.806451612905,16968,20078.709677419352,23928,23260.645161290326,20949.677419354837,14388,9651.4838709677424,6055.2,4068,734,42,42,12,51,32,-5,4.5999999999999996,5.4,9,11.1,14.4,17.8,20.2,19.7,18.3,13.4,8.1999999999999993,5.5,1303.9000000000001,1534.6,"N",8,10,-16,"Pamplona",12.299999999999999,"D","MURCIA",12,12,15,17,21,25,28,28,25,20,16,12,"19.3",1311.9354838709678,2447.8571428571427,4251.6129032258068,4713.333333333333,5577.4193548387093,6646.6666666666661,6461.2903225806458,5819.3548387096771,3996.6666666666665,2680.9677419354839,1682,1130,2.2222222222222223,"Gobierno de Navarra.  Estación Meteorológica del Perdón"]
["Pontevedra",5500,8200,13000,15700,17500,20400,22000,18900,15100,11300,6800,5500,19,42.26,42.43,12,62,27,0,9.1999999999999993,10.1,12.3,14.2,15.6,18.100000000000001,20.2,20.5,18.2,14.9,11.9,9.5,791.4,891,"N",12,10,-4,"Pontevedra",14.558333333333335,"C","NAVARRA",7,7,11,13,16,20,22,23,20,15,10,8,"14.3",1527.7777777777778,2277.7777777777778,3611.1111111111109,4361.1111111111113,4861.1111111111113,5666.666666666667,6111.1111111111113,5250,4194.4444444444443,3138.8888888888887,1888.8888888888889,1527.7777777777778,3.3333333333333335,"Centro de Estudios de la Energía (Ministerio de Industria y Energía) "]
["Salamanca",6100,9500,13500,17100,19700,22800,24600,22600,17500,11300,7400,5200,803,40.58,40.97,18,46,34,-7,3.7,4.9000000000000004,8.1,10.5,13.7,18.399999999999999,21.5,21.2,18.100000000000001,11.9,7.4,4.2,1425.2,1662.2,"O",10,10,-16,"Salamanca",11.966666666666669,"D","ORENSE",9,9,13,15,18,21,24,23,21,16,12,9,"15.8",1694.4444444444443,2638.8888888888887,3750,4750,5472.2222222222217,6333.333333333333,6833.333333333333,6277.7777777777774,4861.1111111111113,3138.8888888888887,2055.5555555555557,1444.4444444444443,2.7777777777777777,"Centro de Estudios de la Energía (Ministerio de Industria y Energía) "]
["Santander",4704,7268,9648,11338,15138,15740,15134,12028,11482,8984,5206,3574,69,43.28,43.47,7,74,25,2,9.3000000000000007,9.1999999999999993,11.5,12.3,14.2,16.899999999999999,18.8,19.3,18.2,15.3,12.2,9.9,634.1,724.1,"O",20,10,-4,"Santander",13.924999999999999,"B","PALENCIA",5,7,10,13,16,20,23,23,20,14,9,6,"13.8",1306.6666666666667,2018.8888888888889,2680,3149.4444444444443,4205,4372.2222222222217,4203.8888888888887,3341.1111111111109,3189.4444444444443,2495.5555555555557,1446.1111111111111,992.77777777777771,5.5555555555555554,"Centro de Estudios de la Energía (Ministerio de Industria y Energía) "]
["Segovia",5700,8800,13400,18400,20400,22600,25700,24900,18800,11400,6800,5100,1002,40.57,40.950000000000003,17,35,33,-6,2.4,4,7.6,10.1,13.2,18.2,21.7,21.3,17.5,11.8,6.6,3.1,1534.1,1366.1,"O",9,10,-17,"Segovia",11.458333333333334,"E","PONTEVEDRA",11,12,14,16,18,20,22,23,20,17,14,12,"16.6",1583.3333333333333,2444.4444444444443,3722.2222222222222,5111.1111111111113,5666.666666666667,6277.7777777777774,7138.8888888888887,6916.6666666666661,5222.2222222222217,3166.6666666666665,1888.8888888888889,1416.6666666666667,2.5,"Centro de Estudios de la Energía (Ministerio de Industria y Energía) "]
["Sevilla",7300,10900,14400,19200,22400,24300,24900,23000,17900,12300,8800,6900,30,37.229999999999997,37.380000000000003,18,43,40,1,10.5,12.3,14.6,17.2,19.899999999999999,24.8,27.9,27.8,24.8,19.8,15,11.4,438.4,438.4,"SO",10,12,-6,"Sevilla",18.833333333333336,"B","SALAMANCA",6,7,10,13,16,20,24,23,20,14,9,6,14,2027.7777777777778,3027.7777777777778,4000,5333.333333333333,6222.2222222222217,6750,6916.6666666666661,6388.8888888888887,4972.2222222222217,3416.6666666666665,2444.4444444444443,1916.6666666666665,2.7777777777777777,"Centro de Estudios de la Energía (Ministerio de Industria y Energía) "]
["Soria",5900,8700,12800,17100,19700,21800,24100,22300,17500,11100,7600,5600,1063,41.46,41.77,18,45,29,-7,2.2999999999999998,3.5,6.6,8.9,11.9,16.5,19.600000000000001,19.5,16.399999999999999,10.9,6.2,3.1,1609.1,1977.6,"VARIA",15,10,-16,"Soria",10.45,"E","SEGOVIA",4,6,10,12,15,20,24,23,20,14,9,5,"13.5",1638.8888888888889,2416.6666666666665,3555.5555555555557,4750,5472.2222222222217,6055.5555555555557,6694.4444444444443,6194.4444444444443,4861.1111111111113,3083.333333333333,2111.1111111111109,1555.5555555555554,4.166666666666667,"Centro de Estudios de la Energía (Ministerio de Industria y Energía) "]
["Tarragona",7414,11544,13168,19200,23000,24800,24100,21000,16400,11600,7800,6100,60,41.07,41.12,7,68,26,1,8.9,10.1,11.6,13.7,16.600000000000001,20.3,22.9,23.2,21.1,17.7,13.2,10.3,583.70000000000005,625.70000000000005,"S",5,10,-7,"Tarragona",15.799999999999999,"B","SEVILLA",11,13,14,17,21,25,29,29,24,20,16,12,"19.3",2059.4444444444443,3206.6666666666665,3657.7777777777778,5333.333333333333,6388.8888888888887,6888.8888888888887,6694.4444444444443,5833.333333333333,4555.5555555555557,3222.2222222222222,2166.6666666666665,1694.4444444444443,1.3888888888888888,"Centro de Estudios de la Energía (Ministerio de Industria y Energía) "]
["Tenerife",10700,13300,18100,21500,25700,26500,29300,26600,21200,16200,10800,9300,37,28.28,28.47,8,55,22,15,17.399999999999999,17.5,18.2,19.2,20.399999999999999,22.4,24.2,24.7,24.1,22.7,20.5,18.399999999999999,241.1,259.10000000000002,"N",18,10,3,"Tenerife",20.80833333333333,"A","SORIA",4,6,9,11,14,19,22,22,18,13,8,5,"12.6",2972.2222222222222,3694.4444444444443,5027.7777777777774,5972.2222222222217,7138.8888888888887,7361.1111111111113,8138.8888888888887,7388.8888888888887,5888.8888888888887,4500,3000,2583.3333333333335,5,"Centro de Estudios de la Energía (Ministerio de Industria y Energía) "]
["Teruel",6100,8800,12900,16700,18400,20600,21800,20700,16900,11000,7100,5300,915,40.21,40.35,14,55,32,-8,1.6,3.5,6.7,9.1,12.9,17.2,19.2,18.899999999999999,16.7,11.1,6.6,3.3,1509.6,1801.7,"SO",1,10,-14,"Teruel",10.566666666666665,"E","STA. C. TENERIFE",19,20,20,21,22,24,26,27,26,25,23,20,"22.8",1694.4444444444443,2444.4444444444443,3583.333333333333,4638.8888888888887,5111.1111111111113,5722.2222222222217,6055.5555555555557,5750,4694.4444444444443,3055.5555555555557,1972.2222222222222,1472.2222222222222,0.27777777777777779,"Centro de Estudios de la Energía (Ministerio de Industria y Energía) "]
["Toledo",6200,9500,14000,19300,21000,24400,27200,24500,18100,11900,7600,5600,540,39.51,39.85,16,34,34,-4,5.9,7.4,10.6,13.4,16.899999999999999,22.1,26.1,25.3,21.2,15.2,9.9,6.4,1089,1158,"E",5,10,-9,"Toledo",15.033333333333333,"C","TARRAGONA",11,12,14,16,19,22,25,26,23,20,15,12,"17.9",1722.2222222222222,2638.8888888888887,3888.8888888888887,5361.1111111111113,5833.333333333333,6777.7777777777774,7555.5555555555557,6805.5555555555557,5027.7777777777774,3305.5555555555557,2111.1111111111109,1555.5555555555554,1.3888888888888888,"Centro de Estudios de la Energía (Ministerio de Industria y Energía) "]
["Valencia",7600,10600,14900,18100,20600,22800,23800,20700,16700,12000,8700,6600,10,39.29,39.479999999999997,11.4,68,32,0,10.3,11,13.1,14.8,17.8,21.9,23.9,24.5,22.4,18.3,14.4,11.1,509.9,515.9,"O",10,10,-8,"Valencia",16.958333333333336,"B","TERUEL",5,6,9,12,16,20,23,24,19,14,9,6,"13.6",2111.1111111111109,2944.4444444444443,4138.8888888888887,5027.7777777777774,5722.2222222222217,6333.333333333333,6611.1111111111113,5750,4638.8888888888887,3333.333333333333,2416.6666666666665,1833.3333333333333,2.7777777777777777,"Centro de Estudios de la Energía (Ministerio de Industria y Energía) "]
["Valladolid",5500,8800,13900,17200,19900,22600,25100,23000,18300,11200,6900,4200,694,41.39,41.65,13,45,33,-5,3.3,5.0999999999999996,8.6,11,14.1,18.5,21.3,20.399999999999999,17.8,12.9,7.7,4.4000000000000004,1444.1,1708.8,"SO",10,10,-16,"Valladolid",12.091666666666667,"D","TOLEDO",5,9,13,15,19,24,28,27,23,17,12,8,"16.9",1527.7777777777778,2444.4444444444443,3861.1111111111109,4777.7777777777774,5527.7777777777774,6277.7777777777774,6972.2222222222217,6388.8888888888887,5083.333333333333,3111.1111111111109,1916.6666666666665,1166.6666666666667,2.7777777777777777,"Centro de Estudios de la Energía (Ministerio de Industria y Energía) "]
["Vitoria",4458,8422,9998,11400,15312,16878,17628,14634,11556,9270,4916,3216,542,42.51,42.85,13,70,26,-4,7.5,11.4,10.8,11.5,13.7,16.2,18.399999999999999,19.3,18.3,15.8,11.9,12.2,1313.8,1599.6,"NE",7,10,-18,"Vitoria",13.916666666666666,"D","VALENCIA",12,13,15,17,20,23,26,27,24,20,16,13,"18.8",1238.3333333333333,2339.4444444444443,2777.2222222222222,3166.6666666666665,4253.333333333333,4688.333333333333,4896.666666666667,4065,3210,2575,1365.5555555555554,893.33333333333326,1.9444444444444444,"Centro de Estudios de la Energía (Ministerio de Industria y Energía) "]
["Vizcaya",5000,7100,10800,12700,15500,16700,17900,15700,13100,9300,6000,4600,32,43.18,43.3,8,71,30,0,7.8,7.7,10.7,11.8,10.5,16.8,15.1,19,18.100000000000001,14.7,10.7,8,735.9,819.9,"NE",7,10,-8,"Vizcaya",12.574999999999998,"C","VALLADOLID",4,6,9,12,17,21,24,23,18,13,8,4,"13.3",1388.8888888888889,1972.2222222222222,3000,3527.7777777777778,4305.5555555555557,4638.8888888888887,4972.2222222222217,4361.1111111111113,3638.8888888888887,2583.3333333333335,1666.6666666666665,1277.7777777777778,1.9444444444444444,"Centro de Estudios de la Energía (Ministerio de Industria y Energía) "]
["Zamora",5400,8900,13200,17300,22200,21600,23500,22000,17200,11100,6700,4600,649,41.3,41.5,18,65,32,-6,3.8,5.3,8.6,11.2,14.2,18.600000000000001,21.6,21.2,18,12.8,7.5,4.3,1303.9000000000001,1501,"O",11,10,-14,"Zamora",12.258333333333335,"D","VIZCAYA",10,11,12,13,16,20,22,22,20,16,13,18,15,1500,2472.2222222222222,3666.6666666666665,4805.5555555555557,6166.6666666666661,6000,6527.7777777777774,6111.1111111111113,4777.7777777777774,3083.333333333333,1861.1111111111111,1277.7777777777778,3.0555555555555554,"Centro de Estudios de la Energía (Ministerio de Industria y Energía) "]
["Zaragoza",6300,9800,15200,18300,21800,24200,25100,23400,18300,12100,7400,5700,200,41.39,41.65,14,57,34,-3,6.1,7.6,11.3,13.7,17,21.2,23.1,23.7,20.6,15.4,10.199999999999999,6.7,1069.5,1150.7,"NO",15,10,-11,"Zaragoza",14.716666666666667,"C","ZAMORA",6,7,11,13,16,21,24,23,20,15,10,6,"14.3",1750,2722.2222222222222,4222.2222222222217,5083.333333333333,6055.5555555555557,6722.2222222222217,6972.2222222222217,6500,5083.333333333333,3361.1111111111109,2055.5555555555557,1583.3333333333333,4.166666666666667,"Centro de Estudios de la Energía (Ministerio de Industria y Energía) "]
["nº DE MES",1,2,3,4,5,6,7,8,9,10,11,12,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"ZARAGOZA",8,10,13,16,19,23,26,26,23,17,12,9,"16.8"]
[]
[]
[]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"40"]
[null,"1","2","3","4","5","6","7","8","9","10","11","12","13","14","15","16","17","18","19","20","21","22","23","24","25","26","27","28","29","30","31","32","33","34","35","36","37","38",null,"39"]
[null,null,"LATITUD = ",28]
[]
[null,"Latitud","Inclinación ","ENE","FEB ","MAR ","ABR ","MAY ","JUN ","JUL ","AGO ","SEP ","OCT ","NOV ","DIC"]
["1","2","3","4","5","6","7","8","9","10","11","12","13","14","15"]
[2800,28,0,1,1,1,1,1,1,1,1,1,1,1,1,null,null,39.6,{"$f":"ROUNDDOWN(R65,0)","v":39}]
[{"$f":"A65+5","v":2805},28,5,1.05,1.04,1.03,1.01,1,1,1,1.02,1.03,1.05,1.06,1.06]
[2810,28,10,1.1000000000000001,1.08,1.05,1.02,1,0.99,1,1.02,1.06,1.1000000000000001,1.1200000000000001,1.1200000000000001]
[2815,28,15,1.1399999999999999,1.1100000000000001,1.07,1.02,0.99,0.98,0.99,1.03,1.08,1.1299999999999999,1.17,1.17]
[2820,28,20,1.17,1.1299999999999999,1.08,1.02,0.97,0.95,0.97,1.02,1.0900000000000001,1.1599999999999999,1.21,1.21]
[2825,28,25,1.2,1.1499999999999999,1.08,1,0.95,0.93,0.95,1.01,1.0900000000000001,1.19,1.25,1.24]
[2830,28,30,1.22,1.1499999999999999,1.07,0.98,0.92,0.89,0.92,0.99,1.0900000000000001,1.2,1.27,1.27]
[2835,28,35,1.23,1.1599999999999999,1.06,0.96,0.88,0.85,0.88,0.96,1.08,1.21,1.29,1.29]
[2840,28,40,1.24,1.1499999999999999,1.04,0.92,0.84,0.8,0.84,0.93,1.06,1.21,1.3,1.3]
[2845,28,45,1.23,1.1399999999999999,1.01,0.89,0.79,0.75,0.79,0.89,1.04,1.2,1.3,1.3]
[2850,28,50,1.22,1.1200000000000001,0.98,0.84,0.73,0.69,0.73,0.84,1,1.18,1.3,1.3]
[2855,28,55,1.2,1.0900000000000001,0.94,0.79,0.68,0.63,0.67,0.79,0.96,1.1499999999999999,1.28,1.28]
[2860,28,60,1.18,1.05,0.9,0.73,0.61,0.56999999999999995,0.61,0.73,0.92,1.1200000000000001,1.26,1.26]
[2865,28,65,1.1399999999999999,1.01,0.85,0.67,0.55000000000000004,0.5,0.54,0.67,0.86,1.08,1.22,1.23]
[2870,28,70,1.1000000000000001,0.97,0.79,0.61,0.48,0.42,0.47,0.6,0.81,1.03,1.18,1.19]
[2875,28,75,1.06,0.91,0.73,0.54,0.4,0.35,0.39,0.53,0.74,0.97,1.1399999999999999,1.1499999999999999]
[2880,28,80,1,0.86,0.66,0.47,0.33,0.27,0.32,0.46,0.67,0.91,1.08,1.1000000000000001]
[2885,28,85,0.94,0.79,0.59,0.39,0.25,0.19,0.24,0.38,0.6,0.84,1.02,1.04]
[2890,28,90,0.88,0.72,0.52,0.32,0.17,0.11,0.16,0.31,0.53,0.77,0.95,0.98]
[2900,29,0,1,1,1,1,1,1,1,1,1,1,1,1]
[{"$f":"A84+5","v":2905},29,5,1.05,1.04,1.03,1.02,1,1,1,1.02,1.03,1.05,1.07,1.06]
[2910,29,10,1.1000000000000001,1.08,1.05,1.02,1,0.99,1,1.03,1.06,1.1000000000000001,1.1200000000000001,1.1200000000000001]
[2915,29,15,1.1499999999999999,1.1100000000000001,1.07,1.03,0.99,0.98,0.99,1.03,1.08,1.1399999999999999,1.18,1.17]
[2920,29,20,1.18,1.1399999999999999,1.08,1.02,0.98,0.95,0.98,1.03,1.1000000000000001,1.17,1.22,1.22]
[2925,29,25,1.21,1.1499999999999999,1.08,1.01,0.95,0.93,0.95,1.01,1.1000000000000001,1.2,1.26,1.25]
[2930,29,30,1.23,1.1599999999999999,1.08,0.99,0.92,0.9,0.92,1,1.1000000000000001,1.21,1.28,1.28]
[2935,29,35,1.24,1.17,1.07,0.97,0.89,0.86,0.89,0.97,1.0900000000000001,1.22,1.3,1.3]
[2940,29,40,1.25,1.1599999999999999,1.05,0.93,0.85,0.81,0.85,0.94,1.07,1.22,1.32,1.31]
[2945,29,45,1.24,1.1499999999999999,1.02,0.9,0.8,0.76,0.8,0.9,1.05,1.21,1.32,1.32]
[2950,29,50,1.23,1.1299999999999999,0.99,0.85,0.75,0.71,0.74,0.85,1.02,1.19,1.31,1.31]
[2955,29,55,1.22,1.1000000000000001,0.95,0.8,0.69,0.64,0.68,0.8,0.98,1.17,1.3,1.3]
[2960,29,60,1.19,1.07,0.91,0.75,0.63,0.57999999999999996,0.62,0.75,0.93,1.1399999999999999,1.28,1.28]
[2965,29,65,1.1599999999999999,1.03,0.86,0.69,0.56000000000000005,0.51,0.55000000000000004,0.69,0.88,1.1000000000000001,1.24,1.25]
[2970,29,70,1.1200000000000001,0.98,0.8,0.62,0.49,0.44,0.48,0.62,0.82,1.05,1.2,1.22]
[2975,29,75,1.07,0.93,0.74,0.55000000000000004,0.42,0.36,0.41,0.55000000000000004,0.76,0.99,1.1599999999999999,1.17]
[2980,29,80,1.02,0.87,0.68,0.48,0.34,0.28000000000000003,0.33,0.48,0.69,0.93,1.1000000000000001,1.1200000000000001]
[2985,29,85,0.96,0.81,0.61,0.41,0.26,0.21,0.25,0.4,0.62,0.87,1.04,1.06]
[2990,29,90,0.9,0.74,0.54,0.33,0.18,0.13,0.17,0.32,0.54,0.79,0.97,1]
[3400,34,0,1,1,1,1,1,1,1,1,1,1,1,1]
[{"$f":"A103+5","v":3405},34,5,1.06,1.05,1.04,1.02,1.01,1.01,1.01,1.02,1.04,1.06,1.08,1.07]
[3410,34,10,1.1200000000000001,1.1000000000000001,1.07,1.04,1.01,1.01,1.02,1.04,1.08,1.1200000000000001,1.1399999999999999,1.1399999999999999]
[3415,34,15,1.17,1.1299999999999999,1.0900000000000001,1.05,1.01,1,1.01,1.05,1.1100000000000001,1.17,1.21,1.2,"DIC"]
[3420,34,20,1.21,1.1599999999999999,1.1100000000000001,1.05,1,0.98,1,1.05,1.1299999999999999,1.21,1.26,1.25,"15"]
[3425,34,25,1.25,1.19,1.1200000000000001,1.04,0.98,0.96,0.99,1.05,1.1399999999999999,1.24,1.31,1.3]
[3430,34,30,1.27,1.2,1.1200000000000001,1.03,0.96,0.94,0.95,1.03,1.1399999999999999,1.27,1.34,1.33]
[3435,34,35,1.29,1.21,1.1100000000000001,1.01,0.93,0.9,0.93,1.01,1.1399999999999999,1.28,1.37,1.36]
[3440,34,40,1.31,1.21,1.1000000000000001,0.98,0.89,0.86,0.89,0.99,1.1299999999999999,1.29,1.39,1.38]
[3445,34,45,1.31,1.21,1.08,0.95,0.85,0.81,0.85,0.95,1.1100000000000001,1.19,1.4,1.4]
[3450,34,50,1.31,1.19,1.05,0.91,0.8,0.76,0.8,0.91,1.0900000000000001,1.28,1.41,1.4]
[3455,34,55,1.3,1.17,1.02,0.86,0.75,0.7,0.75,0.87,1.05,1.26,1.4,1.39]
[3460,34,60,1.28,1.1399999999999999,0.98,0.81,0.69,0.64,0.69,0.82,1.01,1.23,1.38,1.38]
[3465,34,65,1.25,1.1100000000000001,0.93,0.75,0.63,0.57999999999999996,0.62,0.76,0.96,1.2,1.36,1.36]
[3470,34,70,1.21,1.06,0.88,0.69,0.56000000000000005,0.51,0.55000000000000004,0.69,0.91,1.1499999999999999,1.32,1.32]
[3475,34,75,1.17,1.01,0.82,0.63,0.49,0.43,0.48,0.63,0.85,1.1000000000000001,1.28,1.28]
[3480,34,80,1.1200000000000001,0.96,0.76,0.56000000000000005,0.41,0.36,0.41,0.56000000000000005,0.78,1.04,1.23,1.24]
[3485,34,85,1.06,0.9,0.69,0.48,0.34,0.28000000000000003,0.33,0.48,0.71,0.98,1.17,1.18]
[3490,34,90,1,0.83,0.62,0.41,0.26,0.2,0.25,0.4,0.64,0.91,1.1000000000000001,1.1200000000000001]
[3500,35,0,1,1,1,1,1,1,1,1,1,1,1,1]
[{"$f":"A122+5","v":3505},35,5,1.06,1.05,1.04,1.02,1.01,1.01,1.01,1.03,1.04,1.06,1.08,1.07]
[3510,35,10,1.1200000000000001,1.1000000000000001,1.07,1.04,1.02,1.01,1.02,1.04,1.08,1.1200000000000001,1.1499999999999999,1.1399999999999999]
[3515,35,15,1.17,1.1399999999999999,1.0900000000000001,1.05,1.02,1,1.02,1.05,1.1100000000000001,1.17,1.21,1.21]
[3520,35,20,1.22,1.17,1.1100000000000001,1.05,1.01,0.99,1.01,1.06,1.1299999999999999,1.22,1.27,1.26,"15"]
[3525,35,25,1.25,1.2,1.1200000000000001,1.05,0.99,0.97,0.99,1.05,1.1499999999999999,1.25,1.32,1.31]
[3530,35,30,1.28,1.21,1.1299999999999999,1.04,0.97,0.94,0.97,1.04,1.1499999999999999,1.28,1.36,1.35]
[3535,35,35,1.31,1.22,1.1200000000000001,1.02,0.94,0.91,0.94,1.02,1.1499999999999999,1.29,1.39,1.38]
[3540,35,40,1.32,1.23,1.1100000000000001,0.99,0.9,0.87,0.9,1,1.1399999999999999,1.3,1.41,1.4]
[3545,35,45,1.33,1.22,1.0900000000000001,0.96,0.86,0.82,0.86,0.97,1.1299999999999999,1.3,1.42,1.41]
[3550,35,50,1.32,1.21,1.07,0.92,0.81,0.77,0.81,0.93,1.1000000000000001,1.3,1.43,1.42]
[3555,35,55,1.31,1.19,1.03,0.87,0.76,0.72,0.76,0.88,1.07,1.28,1.42,1.41]
[3560,35,60,1.29,1.1599999999999999,0.99,0.82,0.7,0.66,0.7,0.83,1.03,1.25,1.41,1.4]
[3565,35,65,1.27,1.1200000000000001,0.95,0.77,0.64,0.59,0.64,0.77,0.98,1.22,1.38,1.38]
[3570,35,70,1.23,1.08,0.9,0.71,0.56999999999999995,0.52,0.56999999999999995,0.71,0.93,1.18,1.35,1.35]
[3575,35,75,1.19,1.03,0.84,0.64,0.5,0.45,0.5,0.64,0.87,1.1299999999999999,1.31,1.31]
[3580,35,80,1.1399999999999999,0.98,0.78,0.56999999999999995,0.43,0.37,0.42,0.56999999999999995,0.8,1.07,1.26,1.26]
[3585,35,85,1.0900000000000001,0.92,0.71,0.5,0.35,0.28999999999999998,0.34,0.5,0.73,1,1.2,1.21]
[3590,35,90,1.02,0.85,0.64,0.42,0.27,0.21,0.26,0.42,0.66,0.93,1.1299999999999999,1.1499999999999999]
[3600,36,0,1,1,1,1,1,1,1,1,1,1,1,1]
[{"$f":"A141+5","v":3605},36,5,1.07,1.05,1.04,1.02,1.01,1.01,1.01,1.03,1.05,1.07,1.08,1.08]
[3610,36,10,1.1299999999999999,1.1000000000000001,1.07,1.04,1.02,1.01,1.02,1.05,1.08,1.1299999999999999,1.1499999999999999,1.1499999999999999]
[3615,36,15,1.18,1.1399999999999999,1.1000000000000001,1.05,1.02,1.01,1.02,1.06,1.1200000000000001,1.18,1.22,1.21]
[3620,36,20,1.22,1.18,1.1200000000000001,1.06,1.01,0.99,1.01,1.06,1.1399999999999999,1.22,1.28,1.27]
[3625,36,25,1.26,1.2,1.1299999999999999,1.05,1,0.98,1,1.06,1.1599999999999999,1.26,1.33,1.32]
[3630,36,30,1.29,1.22,1.1299999999999999,1.04,0.98,0.95,0.98,1.05,1.1599999999999999,1.29,1.37,1.36]
[3635,36,35,1.32,1.23,1.1299999999999999,1.02,0.95,0.92,0.95,1.03,1.1599999999999999,1.31,1.4,1.39]
[3640,36,40,1.33,1.24,1.1200000000000001,1,0.91,0.88,0.91,1.01,1.1599999999999999,1.32,1.43,1.41]
[3645,36,45,1.34,1.23,1.1000000000000001,0.97,0.87,0.84,0.87,0.98,1.1399999999999999,1.32,1.44,1.43,"15"]
[3650,36,50,1.34,1.22,1.08,0.93,0.82,0.78,0.82,0.94,1.1200000000000001,1.31,1.45,1.44]
[3655,36,55,1.33,1.2,1.05,0.89,0.77,0.73,0.77,0.9,1.08,1.3,1.44,1.43]
[3660,36,60,1.31,1.17,1.01,0.84,0.71,0.67,0.71,0.84,1.05,1.27,1.43,1.42]
[3665,36,65,1.29,1.1399999999999999,0.96,0.78,0.65,0.6,0.65,0.79,1,1.24,1.41,1.4]
[3670,36,70,1.25,1.1000000000000001,0.91,0.72,0.59,0.53,0.57999999999999996,0.73,0.95,1.2,1.37,1.37]
[3675,36,75,1.21,1.05,0.85,0.66,0.52,0.46,0.51,0.66,0.89,1.1499999999999999,1.33,1.33]
[3680,36,80,1.1599999999999999,1,0.79,0.59,0.44,0.39,0.44,0.59,0.82,1.0900000000000001,1.28,1.29]
[3685,36,85,1.1100000000000001,0.94,0.73,0.52,0.37,0.31,0.36,0.51,0.75,1.03,1.23,1.23]
[3690,36,90,1.05,0.87,0.65,0.44,0.28999999999999998,0.23,0.28000000000000003,0.44,0.68,0.96,1.1599999999999999,1.17]
[3700,37,0,1,1,1,1,1,1,1,1,1,1,1,1]
[{"$f":"A160+5","v":3705},37,5,1.07,1.06,1.04,1.03,1.01,1.01,1.02,1.03,1.05,1.07,1.08,1.08]
[3710,37,10,1.1299999999999999,1.1000000000000001,1.08,1.05,1.02,1.01,1.02,1.05,1.0900000000000001,1.1299999999999999,1.1599999999999999,1.1499999999999999]
[3715,37,15,1.18,1.1499999999999999,1.1000000000000001,1.06,1.02,1.01,1.02,1.06,1.1200000000000001,1.19,1.23,1.22]
[3720,37,20,1.23,1.18,1.1200000000000001,1.06,1.02,1,1.02,1.07,1.1499999999999999,1.23,1.29,1.28]
[3725,37,25,1.27,1.21,1.1399999999999999,1.06,1,0.98,1,1.07,1.1599999999999999,1.27,1.34,1.33]
[3730,37,30,1.3,1.23,1.1399999999999999,1.05,0.98,0.96,0.98,1.06,1.17,1.3,1.38,1.37]
[3735,37,35,1.33,1.24,1.1399999999999999,1.03,0.96,0.93,0.96,1.04,1.17,1.32,1.42,1.41]
[3740,37,40,1.35,1.25,1.1299999999999999,1.01,0.92,0.89,0.92,1.02,1.17,1.34,1.44,1.43]
[3745,37,45,1.35,1.25,1.1100000000000001,0.98,0.88,0.85,0.88,0.99,1.1499999999999999,1.34,1.46,1.45]
[3750,37,50,1.35,1.24,1.0900000000000001,0.94,0.84,0.8,0.84,0.95,1.1299999999999999,1.33,1.47,1.46]
[3755,37,55,1.35,1.22,1.06,0.9,0.78,0.74,0.78,0.91,1.1000000000000001,1.32,1.47,1.45]
[3760,37,60,1.33,1.19,1.02,0.85,0.73,0.68,0.73,0.86,1.06,1.3,1.45,1.44]
[3765,37,65,1.31,1.1599999999999999,0.98,0.8,0.67,0.62,0.66,0.8,1.02,1.26,1.43,1.42]
[3770,37,70,1.27,1.1200000000000001,0.93,0.74,0.6,0.55000000000000004,0.6,0.74,0.97,1.22,1.4,1.4,"15"]
[3775,37,75,1.23,1.07,0.87,0.67,0.53,0.48,0.53,0.68,0.91,1.17,1.36,1.36]
[3780,37,80,1.19,1.02,0.81,0.6,0.46,0.4,0.45,0.6,0.84,1.1200000000000001,1.31,1.31]
[3785,37,85,1.1299999999999999,0.96,0.74,0.53,0.38,0.32,0.38,0.53,0.77,1.05,1.26,1.26]
[3790,37,90,1.07,0.89,0.67,0.46,0.3,0.25,0.3,0.45,0.7,0.98,1.19,1.2]
[3800,38,0,1,1,1,1,1,1,1,1,1,1,1,1]
[{"$f":"A179+5","v":3805},38,5,1.07,1.06,1.04,1.03,1.02,1.01,1.02,1.03,1.05,1.07,1.08,1.08]
[3810,38,10,1.1299999999999999,1.1100000000000001,1.08,1.05,1.02,1.02,1.03,1.05,1.0900000000000001,1.1399999999999999,1.1599999999999999,1.1599999999999999]
[3815,38,15,1.19,1.1499999999999999,1.1100000000000001,1.06,1.03,1.01,1.03,1.07,1.1299999999999999,1.19,1.23,1.22]
[3820,38,20,1.24,1.19,1.1299999999999999,1.07,1.02,1.01,1.02,1.07,1.1499999999999999,1.24,1.3,1.29]
[3825,38,25,1.28,1.22,1.1399999999999999,1.07,1.01,0.99,1.01,1.08,1.17,1.28,1.35,1.34]
[3830,38,30,1.31,1.24,1.1499999999999999,1.06,0.99,0.97,0.99,1.07,1.18,1.31,1.4,1.38]
[3835,38,35,1.34,1.25,1.1499999999999999,1.04,0.96,0.94,0.97,1.05,1.19,1.34,1.43,1.42]
[3840,38,40,1.36,1.26,1.1399999999999999,1.02,0.93,0.9,0.93,1.03,1.18,1.35,1.46,1.45]
[3845,38,45,1.37,1.26,1.1299999999999999,0.99,0.89,0.86,0.89,1,1.17,1.36,1.48,1.47]
[3850,38,50,1.37,1.25,1.1000000000000001,0.95,0.85,0.81,0.85,0.97,1.1499999999999999,1.35,1.49,1.48]
[3855,38,55,1.36,1.23,1.07,0.91,0.8,0.75,0.8,0.92,1.1200000000000001,1.34,1.49,1.48]
[3860,38,60,1.35,1.21,1.04,0.86,0.74,0.69,0.74,0.87,1.08,1.32,1.48,1.47]
[3865,38,65,1.33,1.18,0.99,0.81,0.68,0.63,0.68,0.82,1.04,1.29,1.46,1.45]
[3870,38,70,1.29,1.1399999999999999,0.94,0.75,0.61,0.56000000000000005,0.61,0.76,0.98,1.25,1.43,1.42]
[3875,38,75,1.25,1.0900000000000001,0.89,0.69,0.54,0.49,0.54,0.69,0.93,1.2,1.39,1.39]
[3880,38,80,1.21,1.04,0.83,0.62,0.47,0.42,0.47,0.62,0.86,1.1399999999999999,1.34,1.34]
[3885,38,85,1.1499999999999999,0.98,0.76,0.55000000000000004,0.4,0.34,0.39,0.55000000000000004,0.79,1.08,1.29,1.29]
[3890,38,90,1.0900000000000001,0.91,0.69,0.47,0.32,0.26,0.31,0.47,0.72,1.01,1.22,1.23]
[3900,39,0,1,1,1,1,1,1,1,1,1,1,1,1]
[{"$f":"A198+5","v":3905},39,5,1.07,1.06,1.04,1.03,1.02,1.01,1.02,1.03,1.05,1.07,1.0900000000000001,1.08]
[3910,39,10,1.1399999999999999,1.1100000000000001,1.08,1.05,1.03,1.02,1.03,1.06,1.1000000000000001,1.1399999999999999,1.17,1.1599999999999999]
[3915,39,15,1.19,1.1599999999999999,1.1100000000000001,1.07,1.03,1.02,1.03,1.07,1.1299999999999999,1.2,1.24,1.23]
[3920,39,20,1.25,1.2,1.1399999999999999,1.07,1.03,1.01,1.03,1.08,1.1100000000000001,1.25,1.31,1.29]
[3925,39,25,1.29,1.23,1.1499999999999999,1.07,1.02,1,1.02,1.08,1.18,1.29,1.36,1.35]
[3930,39,30,1.33,1.25,1.1599999999999999,1.07,1,0.97,1,1.08,1.19,1.33,1.41,1.4]
[3935,39,35,1.35,1.27,1.1599999999999999,1.05,0.97,0.94,0.98,1.06,1.2,1.35,1.45,1.43]
[3940,39,40,1.37,1.27,1.1499999999999999,1.03,0.94,0.91,0.94,1.04,1.19,1.37,1.48,1.46]
[3945,39,45,1.38,1.27,1.1399999999999999,1,0.9,0.87,0.9,1.01,1.18,1.37,1.5,1.48]
[3950,39,50,1.39,1.26,1.1200000000000001,0.97,0.86,0.82,0.86,0.98,1.1599999999999999,1.37,1.51,1.5]
[3955,39,55,1.38,1.25,1.0900000000000001,0.93,0.81,0.77,0.81,0.94,1.1299999999999999,1.36,1.51,1.5]
[3960,39,60,1.37,1.22,1.05,0.88,0.75,0.71,0.75,0.89,1.1000000000000001,1.34,1.51,1.49]
[3965,39,65,1.35,1.19,1.01,0.83,0.69,0.65,0.69,0.83,1.05,1.31,1.49,1.47]
[3970,39,70,1.32,1.1499999999999999,0.96,0.77,0.63,0.57999999999999996,0.63,0.77,1,1.27,1.46,1.45]
[3975,39,75,1.28,1.1100000000000001,0.91,0.7,0.56000000000000005,0.51,0.56000000000000005,0.71,0.95,1.23,1.42,1.41]
[3980,39,80,1.23,1.06,0.84,0.64,0.49,0.43,0.48,0.64,0.88,1.17,1.37,1.37]
[3985,39,85,1.18,1,0.78,0.56000000000000005,0.41,0.35,0.41,0.56000000000000005,0.81,1.1100000000000001,1.32,1.32]
[3990,39,90,1.1200000000000001,0.93,0.71,0.49,0.33,0.28000000000000003,0.33,0.49,0.74,1.04,1.25,1.26]
[4000,40,"00",1,1,1,1,1,1,1,1,1,1,1,1]
[{"$f":"A217+5","v":4005},40,"05",1.07,1.06,1.05,1.03,1.02,1.01,1.02,1.03,1.05,1.08,1.0900000000000001,1.0900000000000001]
[4010,40,10,1.1399999999999999,1.1100000000000001,1.08,1.05,1.03,1.02,1.03,1.06,1.1000000000000001,1.1399999999999999,1.17,1.1599999999999999]
[4015,40,15,1.2,1.1599999999999999,1.1200000000000001,1.07,1.03,1.02,1.04,1.08,1.1399999999999999,1.21,1.25,1.24]
[4020,40,20,1.25,1.2,1.1399999999999999,1.08,1.03,1.02,1.03,1.0900000000000001,1.17,1.26,1.32,1.3]
[4025,40,25,1.3,1.23,1.1599999999999999,1.08,1.02,1,1.02,1.0900000000000001,1.19,1.3,1.38,1.36]
[4030,40,30,1.34,1.26,1.17,1.07,1.01,0.98,1.01,1.0900000000000001,1.2,1.34,1.43,1.41]
[4035,40,35,1.37,1.28,1.17,1.06,0.98,0.95,0.98,1.07,1.21,1.37,1.47,1.45]
[4040,40,40,1.39,1.29,1.1599999999999999,1.04,0.95,0.92,0.95,1.05,1.21,1.39,1.5,1.48]
[4045,40,45,1.4,1.29,1.1499999999999999,1.01,0.91,0.88,0.92,1.03,1.2,1.39,1.52,1.5]
[4050,40,50,1.41,1.28,1.1299999999999999,0.98,0.87,0.83,0.87,0.99,1.18,1.39,1.54,1.52]
[4055,40,55,1.4,1.27,1.1000000000000001,0.94,0.82,0.78,0.82,0.95,1.1100000000000001,1.38,1.54,1.52]
[4060,40,60,1.39,1.24,1.07,0.89,0.77,0.72,0.77,0.9,1.1200000000000001,1.36,1.53,1.51]
[4065,40,65,1.37,1.21,1.03,0.84,0.71,0.66,0.71,0.85,1.07,1.34,1.51,1.5]
[4070,40,70,1.34,1.17,0.98,0.78,0.64,0.59,0.64,0.79,1.02,1.3,1.49,1.47]
[4075,40,75,1.3,1.1299999999999999,0.92,0.72,0.56999999999999995,0.52,0.56999999999999995,0.73,0.97,1.25,1.45,1.44]
[4080,40,80,1.25,1.08,0.86,0.65,0.5,0.45,0.5,0.66,0.9,1.2,1.41,1.4]
[4085,40,85,1.2,1.02,0.8,0.57999999999999996,0.43,0.37,0.42,0.57999999999999996,0.84,1.1399999999999999,1.35,1.35]
[4090,40,90,1.1399999999999999,0.95,0.73,0.5,0.35,0.28999999999999998,0.34,0.5,0.76,1.07,1.29,1.29]
[4100,41,0,1,1,1,1,1,1,1,1,1,1,1,1]
[{"$f":"A236+5","v":4105},41,5,1.07,1.06,1.05,1.03,1.02,1.02,1.02,1.03,1.05,1.08,1.0900000000000001,1.0900000000000001]
[4110,41,10,1.1399999999999999,1.1200000000000001,1.0900000000000001,1.06,1.03,1.02,1.03,1.06,1.1000000000000001,1.1499999999999999,1.18,1.17]
[4115,41,15,1.21,1.17,1.1200000000000001,1.07,1.04,1.03,1.04,1.08,1.1399999999999999,1.21,1.26,1.24]
[4120,41,20,1.26,1.21,1.1499999999999999,1.08,1.04,1.02,1.04,1.0900000000000001,1.17,1.27,1.33,1.31]
[4125,41,25,1.31,1.24,1.17,1.0900000000000001,1.03,1.01,1.03,1.1000000000000001,1.2,1.32,1.39,1.37]
[4130,41,30,1.35,1.27,1.18,1.08,1.01,0.99,1.02,1.0900000000000001,1.21,1.35,1.44,1.42]
[4135,41,35,1.38,1.29,1.18,1.07,0.99,0.96,0.99,1.08,1.22,1.38,1.49,1.47]
[4140,41,40,1.4,1.3,1.18,1.05,0.95,0.93,0.95,1.06,1.22,1.4,1.52,1.5]
[4145,41,45,1.42,1.3,1.1599999999999999,1.03,0.93,0.89,0.93,1.04,1.21,1.41,1.55,1.52]
[4150,41,50,1.42,1.3,1.1399999999999999,0.99,0.88,0.84,0.88,1.01,1.19,1.41,1.56,1.54]
[4155,41,55,1.42,1.28,1.1200000000000001,0.95,0.83,0.79,0.84,0.97,1.17,1.41,1.57,1.54]
[4160,41,60,1.41,1.26,1.08,0.91,0.78,0.73,0.78,0.92,1.1399999999999999,1.39,1.56,1.54]
[4165,41,65,1.39,1.23,1.04,0.85,0.72,0.67,0.72,0.87,1.0900000000000001,1.36,1.54,1.53]
[4170,41,70,1.36,1.19,0.99,0.8,0.66,0.61,0.66,0.81,1.04,1.32,1.52,1.5]
[4175,41,75,1.32,1.1499999999999999,0.94,0.73,0.59,0.54,0.59,0.74,0.99,1.28,1.48,1.47]
[4180,41,80,1.28,1.1000000000000001,0.88,0.67,0.52,0.46,0.52,0.67,0.93,1.23,1.44,1.43]
[4185,41,85,1.23,1.04,0.82,0.6,0.44,0.39,0.44,0.6,0.86,1.1599999999999999,1.38,1.38]
[4190,41,90,1.17,0.98,0.74,0.52,0.36,0.31,0.36,0.52,0.78,1.0900000000000001,1.32,1.32]
[4200,42,0,1,1,1,1,1,1,1,1,1,1,1,1]
[{"$f":"A255+5","v":4205},42,5,1.08,1.06,1.05,1.03,1.02,1.02,1.02,1.04,1.06,1.08,1.0900000000000001,1.0900000000000001]
[4210,42,10,1.1499999999999999,1.1200000000000001,1.0900000000000001,1.06,1.04,1.03,1.04,1.06,1.1100000000000001,1.1499999999999999,1.18,1.17]
[4215,42,15,1.21,1.17,1.1299999999999999,1.08,1.04,1.03,1.04,1.0900000000000001,1.1499999999999999,1.22,1.26,1.25]
[4220,42,20,1.27,1.21,1.1499999999999999,1.0900000000000001,1.04,1.03,1.05,1.1000000000000001,1.18,1.28,1.34,1.32]
[4225,42,25,1.32,1.25,1.17,1.0900000000000001,1.04,1.01,1.04,1.1000000000000001,1.21,1.33,1.4,1.38]
[4230,42,30,1.36,1.28,1.19,1.0900000000000001,1.02,1,1.02,1.1000000000000001,1.23,1.37,1.46,1.44]
[4235,42,35,1.39,1.3,1.19,1.08,1,0.97,1,1.0900000000000001,1.23,1.4,1.51,1.48]
[4240,42,40,1.42,1.31,1.19,1.06,0.97,0.94,0.97,1.08,1.24,1.42,1.54,1.52]
[4245,42,45,1.43,1.32,1.18,1.04,0.94,0.9,0.94,1.05,1.23,1.43,1.57,1.54]
[4250,42,50,1.44,1.31,1.1599999999999999,1,0.89,0.86,0.9,1.02,1.21,1.44,1.59,1.56]
[4255,42,55,1.44,1.3,1.1299999999999999,0.97,0.85,0.8,0.85,0.98,1.19,1.43,1.59,1.57]
[4260,42,60,1.43,1.28,1.1000000000000001,0.92,0.79,0.75,0.8,0.93,1.1499999999999999,1.41,1.59,1.57]
[4265,42,65,1.41,1.25,1.06,0.87,0.74,0.69,0.74,0.88,1.1100000000000001,1.39,1.57,1.55]
[4270,42,70,1.38,1.21,1.01,0.81,0.67,0.62,0.67,0.82,1.07,1.35,1.55,1.53]
[4275,42,75,1.35,1.17,0.96,0.75,0.6,0.55000000000000004,0.6,0.76,1.01,1.31,1.52,1.5]
[4280,42,80,1.3,1.1200000000000001,0.9,0.68,0.53,0.48,0.53,0.69,0.95,1.25,1.47,1.46]
[4285,42,85,1.25,1.06,0.83,0.61,0.46,0.4,0.46,0.62,0.88,1.19,1.42,1.41]
[4290,42,90,1.19,1,0.76,0.54,0.38,0.32,0.38,0.54,0.81,1.1200000000000001,1.36,1.35]
[4300,43,0,1,1,1,1,1,1,1,1,1,1,1,1]
[{"$f":"A274+5","v":4305},43,5,1.08,1.07,1.05,1.03,1.02,1.02,1.02,1.04,1.06,1.08,1.1000000000000001,1.0900000000000001]
[4310,43,10,1.1499999999999999,1.1200000000000001,1.0900000000000001,1.06,1.04,1.03,1.04,1.07,1.1100000000000001,1.1599999999999999,1.19,1.18]
[4315,43,15,1.22,1.18,1.1299999999999999,1.08,1.05,1.03,1.05,1.0900000000000001,1.1499999999999999,1.23,1.27,1.26]
[4320,43,20,1.28,1.22,1.1599999999999999,1.0900000000000001,1.05,1.03,1.05,1.1000000000000001,1.19,1.29,1.35,1.33]
[4325,43,25,1.33,1.26,1.18,1.1000000000000001,1.04,1.02,1.04,1.1100000000000001,1.22,1.34,1.42,1.4]
[4330,43,30,1.37,1.29,1.2,1.1000000000000001,1.03,1,1.03,1.1100000000000001,1.24,1.38,1.48,1.45]
[4335,43,35,1.41,1.31,1.2,1.0900000000000001,1.01,0.98,1.01,1.1000000000000001,1.25,1.42,1.52,1.5]
[4340,43,40,1.43,1.33,1.2,1.07,0.98,0.95,0.98,1.0900000000000001,1.25,1.44,1.56,1.54]
[4345,43,45,1.45,1.33,1.19,1.05,0.95,0.91,0.95,1.06,1.24,1.45,1.59,1.57]
[4350,43,50,1.46,1.33,1.17,1.02,0.91,0.87,0.91,1.03,1.23,1.46,1.61,1.58]
[4355,43,55,1.46,1.32,1.1499999999999999,0.98,0.86,0.82,0.86,1,1.21,1.45,1.62,1.59]
[4360,43,60,1.45,1.3,1.1200000000000001,0.94,0.81,0.76,0.81,0.95,1.17,1.44,1.62,1.59]
[4365,43,65,1.43,1.27,1.08,0.89,0.75,0.7,0.75,0.9,1.1299999999999999,1.41,1.61,1.58]
[4370,43,70,1.41,1.23,1.03,0.83,0.69,0.64,0.69,0.84,1.0900000000000001,1.38,1.58,1.56]
[4375,43,75,1.37,1.19,0.98,0.77,0.62,0.56999999999999995,0.62,0.78,1.03,1.34,1.55,1.53]
[4380,43,80,1.33,1.1399999999999999,0.92,0.7,0.55000000000000004,0.49,0.55000000000000004,0.71,0.97,1.28,1.51,1.49]
[4385,43,85,1.28,1.08,0.85,0.63,0.47,0.42,0.47,0.64,0.9,1.22,1.45,1.44]
[4390,43,90,1.22,1.02,0.78,0.56000000000000005,0.4,0.34,0.39,0.56000000000000005,0.83,1.1599999999999999,1.39,1.38]

{"sheet":"GRÀFICA","index":7,"n_rows":20,"n_cols":12,"rows_kept":20,"cut":false,"hidden":true,"merged":[[0,0,0,12]]}
[]
[]
[]
[]
[]
[]
[null,null,"MESOS","Tm","Ta","Tg","Ts",null,null,"Prof","ξ","Tg"]
[null,null,"Gen",{"$f":"'2.CLIMA'!I12","v":9.4},{"$f":"D8+('2.CLIMA'!$K$19-D8)*COS((2*PI()*((365*3600)/PARÀMETRES!$D$38)))","v":30.263997847843875},{"$f":"D20+(D8-D20)*EXP(-('4.CONDUCTES'!$E$26/(SQRT(('3.TERRENY'!$K$19*PARÀMETRES!$D$38)/(PI()*'3.TERRENY'!$K$16*'3.TERRENY'!$K$22)))))*COS((2*PI()*(1/PARÀMETRES!$D$38))-('4.CONDUCTES'!$E$26/(SQRT(('3.TERRENY'!$K$19*PARÀMETRES!$D$38)/(PI()*'3.TERRENY'!$K$16*'3.TERRENY'!$K$22)))))","v":14.234120175864884},{"$f":"F8-(F8-D8)*EXP(-((3600*'5.CÀLCUL'!$M$23*PI()*'4.CONDUCTES'!$E$30*'4.CONDUCTES'!$E$28)/(PARÀMETRES!$D$30*PARÀMETRES!$D$31*'5.CÀLCUL'!$H$28)))","v":10.471094684803862},null,null,0,{"$f":"J8/(SQRT(('3.TERRENY'!$K$19*PARÀMETRES!$D$38)/(PI()*'3.TERRENY'!$K$16*'3.TERRENY'!$K$22)))","v":0},{"$f":"$D$20+('5.CÀLCUL'!$M$8-$D$20)*(EXP(-($K8))*COS((2*PI()*(1/PARÀMETRES!$D$38))-($K8)))","v":30.999999999999709}]
[null,null,"Feb",{"$f":"'2.CLIMA'!I13","v":9.9},{"$f":"D9+('2.CLIMA'!$K$19-D9)*COS((2*PI()*((365*3600)/PARÀMETRES!$D$38)))","v":30.281034934699342},{"$f":"$D$20+(D9-$D$20)*EXP(-('4.CONDUCTES'!$E$26/(SQRT(('3.TERRENY'!$K$19*PARÀMETRES!$D$38)/(PI()*'3.TERRENY'!$K$16*'3.TERRENY'!$K$22)))))*COS((2*PI()*(1/PARÀMETRES!$D$38))-('4.CONDUCTES'!$E$26/(SQRT(('3.TERRENY'!$K$19*PARÀMETRES!$D$38)/(PI()*'3.TERRENY'!$K$16*'3.TERRENY'!$K$22)))))","v":14.389646054069285},{"$f":"F9-(F9-D9)*EXP(-((3600*'5.CÀLCUL'!$M$23*PI()*'4.CONDUCTES'!$E$30*'4.CONDUCTES'!$E$28)/(PARÀMETRES!$D$30*PARÀMETRES!$D$31*'5.CÀLCUL'!$H$28)))","v":10.89476964788197},null,null,1,{"$f":"J9/(SQRT(('3.TERRENY'!$K$19*PARÀMETRES!$D$38)/(PI()*'3.TERRENY'!$K$16*'3.TERRENY'!$K$22)))","v":0.40157544603426276},{"$f":"$D$20+('5.CÀLCUL'!$M$8-$D$20)*(EXP(-($K9))*COS((2*PI()*(1/PARÀMETRES!$D$38))-($K9)))","v":25.400326851451926}]
[null,null,"Mar",{"$f":"'2.CLIMA'!I14","v":12.3},{"$f":"D10+('2.CLIMA'!$K$19-D10)*COS((2*PI()*((365*3600)/PARÀMETRES!$D$38)))","v":30.362812951605576},{"$f":"$D$20+(D10-$D$20)*EXP(-('4.CONDUCTES'!$E$26/(SQRT(('3.TERRENY'!$K$19*PARÀMETRES!$D$38)/(PI()*'3.TERRENY'!$K$16*'3.TERRENY'!$K$22)))))*COS((2*PI()*(1/PARÀMETRES!$D$38))-('4.CONDUCTES'!$E$26/(SQRT(('3.TERRENY'!$K$19*PARÀMETRES!$D$38)/(PI()*'3.TERRENY'!$K$16*'3.TERRENY'!$K$22)))))","v":15.136170269450417},{"$f":"F10-(F10-D10)*EXP(-((3600*'5.CÀLCUL'!$M$23*PI()*'4.CONDUCTES'!$E$30*'4.CONDUCTES'!$E$28)/(PARÀMETRES!$D$30*PARÀMETRES!$D$31*'5.CÀLCUL'!$H$28)))","v":12.928409470656897},null,null,2,{"$f":"J10/(SQRT(('3.TERRENY'!$K$19*PARÀMETRES!$D$38)/(PI()*'3.TERRENY'!$K$16*'3.TERRENY'!$K$22)))","v":0.80315089206852552},{"$f":"$D$20+('5.CÀLCUL'!$M$8-$D$20)*(EXP(-($K10))*COS((2*PI()*(1/PARÀMETRES!$D$38))-($K10)))","v":20.952838114295069}]
[null,null,"Abr",{"$f":"'2.CLIMA'!I15","v":14.6},{"$f":"D11+('2.CLIMA'!$K$19-D11)*COS((2*PI()*((365*3600)/PARÀMETRES!$D$38)))","v":30.441183551140718},{"$f":"$D$20+(D11-$D$20)*EXP(-('4.CONDUCTES'!$E$26/(SQRT(('3.TERRENY'!$K$19*PARÀMETRES!$D$38)/(PI()*'3.TERRENY'!$K$16*'3.TERRENY'!$K$22)))))*COS((2*PI()*(1/PARÀMETRES!$D$38))-('4.CONDUCTES'!$E$26/(SQRT(('3.TERRENY'!$K$19*PARÀMETRES!$D$38)/(PI()*'3.TERRENY'!$K$16*'3.TERRENY'!$K$22)))))","v":15.851589309190668},{"$f":"F11-(F11-D11)*EXP(-((3600*'5.CÀLCUL'!$M$23*PI()*'4.CONDUCTES'!$E$30*'4.CONDUCTES'!$E$28)/(PARÀMETRES!$D$30*PARÀMETRES!$D$31*'5.CÀLCUL'!$H$28)))","v":14.877314300816201},null,null,3,{"$f":"J11/(SQRT(('3.TERRENY'!$K$19*PARÀMETRES!$D$38)/(PI()*'3.TERRENY'!$K$16*'3.TERRENY'!$K$22)))","v":1.2047263381027882},{"$f":"$D$20+('5.CÀLCUL'!$M$8-$D$20)*(EXP(-($K11))*COS((2*PI()*(1/PARÀMETRES!$D$38))-($K11)))","v":17.981512960856108}]
[null,null,"Mai",{"$f":"'2.CLIMA'!I16","v":17.7},{"$f":"D12+('2.CLIMA'!$K$19-D12)*COS((2*PI()*((365*3600)/PARÀMETRES!$D$38)))","v":30.546813489644606},{"$f":"$D$20+(D12-$D$20)*EXP(-('4.CONDUCTES'!$E$26/(SQRT(('3.TERRENY'!$K$19*PARÀMETRES!$D$38)/(PI()*'3.TERRENY'!$K$16*'3.TERRENY'!$K$22)))))*COS((2*PI()*(1/PARÀMETRES!$D$38))-('4.CONDUCTES'!$E$26/(SQRT(('3.TERRENY'!$K$19*PARÀMETRES!$D$38)/(PI()*'3.TERRENY'!$K$16*'3.TERRENY'!$K$22)))))","v":16.815849754057965},{"$f":"F12-(F12-D12)*EXP(-((3600*'5.CÀLCUL'!$M$23*PI()*'4.CONDUCTES'!$E$30*'4.CONDUCTES'!$E$28)/(PARÀMETRES!$D$30*PARÀMETRES!$D$31*'5.CÀLCUL'!$H$28)))","v":17.50409907190048},null,null,4,{"$f":"J12/(SQRT(('3.TERRENY'!$K$19*PARÀMETRES!$D$38)/(PI()*'3.TERRENY'!$K$16*'3.TERRENY'!$K$22)))","v":1.606301784137051},{"$f":"$D$20+('5.CÀLCUL'!$M$8-$D$20)*(EXP(-($K12))*COS((2*PI()*(1/PARÀMETRES!$D$38))-($K12)))","v":16.312806210723384}]
[null,null,"Jun",{"$f":"'2.CLIMA'!I17","v":21.6},{"$f":"D13+('2.CLIMA'!$K$19-D13)*COS((2*PI()*((365*3600)/PARÀMETRES!$D$38)))","v":30.679702767117242},{"$f":"$D$20+(D13-$D$20)*EXP(-('4.CONDUCTES'!$E$26/(SQRT(('3.TERRENY'!$K$19*PARÀMETRES!$D$38)/(PI()*'3.TERRENY'!$K$16*'3.TERRENY'!$K$22)))))*COS((2*PI()*(1/PARÀMETRES!$D$38))-('4.CONDUCTES'!$E$26/(SQRT(('3.TERRENY'!$K$19*PARÀMETRES!$D$38)/(PI()*'3.TERRENY'!$K$16*'3.TERRENY'!$K$22)))))","v":18.028951604052306},{"$f":"F13-(F13-D13)*EXP(-((3600*'5.CÀLCUL'!$M$23*PI()*'4.CONDUCTES'!$E$30*'4.CONDUCTES'!$E$28)/(PARÀMETRES!$D$30*PARÀMETRES!$D$31*'5.CÀLCUL'!$H$28)))","v":20.80876378390974},null,null,5,{"$f":"J13/(SQRT(('3.TERRENY'!$K$19*PARÀMETRES!$D$38)/(PI()*'3.TERRENY'!$K$16*'3.TERRENY'!$K$22)))","v":2.0078772301713137},{"$f":"$D$20+('5.CÀLCUL'!$M$8-$D$20)*(EXP(-($K13))*COS((2*PI()*(1/PARÀMETRES!$D$38))-($K13)))","v":15.587787178247689}]
[null,null,"Jul",{"$f":"'2.CLIMA'!I18","v":24.4},{"$f":"D14+('2.CLIMA'!$K$19-D14)*COS((2*PI()*((365*3600)/PARÀMETRES!$D$38)))","v":30.77511045350785},{"$f":"$D$20+(D14-$D$20)*EXP(-('4.CONDUCTES'!$E$26/(SQRT(('3.TERRENY'!$K$19*PARÀMETRES!$D$38)/(PI()*'3.TERRENY'!$K$16*'3.TERRENY'!$K$22)))))*COS((2*PI()*(1/PARÀMETRES!$D$38))-('4.CONDUCTES'!$E$26/(SQRT(('3.TERRENY'!$K$19*PARÀMETRES!$D$38)/(PI()*'3.TERRENY'!$K$16*'3.TERRENY'!$K$22)))))","v":18.899896521996958},{"$f":"F14-(F14-D14)*EXP(-((3600*'5.CÀLCUL'!$M$23*PI()*'4.CONDUCTES'!$E$30*'4.CONDUCTES'!$E$28)/(PARÀMETRES!$D$30*PARÀMETRES!$D$31*'5.CÀLCUL'!$H$28)))","v":23.18134357714715},null,null,6,{"$f":"J14/(SQRT(('3.TERRENY'!$K$19*PARÀMETRES!$D$38)/(PI()*'3.TERRENY'!$K$16*'3.TERRENY'!$K$22)))","v":2.4094526762055763},{"$f":"$D$20+('5.CÀLCUL'!$M$8-$D$20)*(EXP(-($K14))*COS((2*PI()*(1/PARÀMETRES!$D$38))-($K14)))","v":15.441970766738375}]
[null,null,"Ago",{"$f":"'2.CLIMA'!I19","v":24.2},{"$f":"D15+('2.CLIMA'!$K$19-D15)*COS((2*PI()*((365*3600)/PARÀMETRES!$D$38)))","v":30.768295618765663},{"$f":"$D$20+(D15-$D$20)*EXP(-('4.CONDUCTES'!$E$26/(SQRT(('3.TERRENY'!$K$19*PARÀMETRES!$D$38)/(PI()*'3.TERRENY'!$K$16*'3.TERRENY'!$K$22)))))*COS((2*PI()*(1/PARÀMETRES!$D$38))-('4.CONDUCTES'!$E$26/(SQRT(('3.TERRENY'!$K$19*PARÀMETRES!$D$38)/(PI()*'3.TERRENY'!$K$16*'3.TERRENY'!$K$22)))))","v":18.837686170715198},{"$f":"F15-(F15-D15)*EXP(-((3600*'5.CÀLCUL'!$M$23*PI()*'4.CONDUCTES'!$E$30*'4.CONDUCTES'!$E$28)/(PARÀMETRES!$D$30*PARÀMETRES!$D$31*'5.CÀLCUL'!$H$28)))","v":23.011873591915908},null,null,7,{"$f":"J15/(SQRT(('3.TERRENY'!$K$19*PARÀMETRES!$D$38)/(PI()*'3.TERRENY'!$K$16*'3.TERRENY'!$K$22)))","v":2.811028122239839},{"$f":"$D$20+('5.CÀLCUL'!$M$8-$D$20)*(EXP(-($K15))*COS((2*PI()*(1/PARÀMETRES!$D$38))-($K15)))","v":15.587065620399683}]
[null,null,"Set",{"$f":"'2.CLIMA'!I20","v":21.7},{"$f":"D16+('2.CLIMA'!$K$19-D16)*COS((2*PI()*((365*3600)/PARÀMETRES!$D$38)))","v":30.683110184488335},{"$f":"$D$20+(D16-$D$20)*EXP(-('4.CONDUCTES'!$E$26/(SQRT(('3.TERRENY'!$K$19*PARÀMETRES!$D$38)/(PI()*'3.TERRENY'!$K$16*'3.TERRENY'!$K$22)))))*COS((2*PI()*(1/PARÀMETRES!$D$38))-('4.CONDUCTES'!$E$26/(SQRT(('3.TERRENY'!$K$19*PARÀMETRES!$D$38)/(PI()*'3.TERRENY'!$K$16*'3.TERRENY'!$K$22)))))","v":18.060056779693184},{"$f":"F16-(F16-D16)*EXP(-((3600*'5.CÀLCUL'!$M$23*PI()*'4.CONDUCTES'!$E$30*'4.CONDUCTES'!$E$28)/(PARÀMETRES!$D$30*PARÀMETRES!$D$31*'5.CÀLCUL'!$H$28)))","v":20.893498776525359},null,null,8,{"$f":"J16/(SQRT(('3.TERRENY'!$K$19*PARÀMETRES!$D$38)/(PI()*'3.TERRENY'!$K$16*'3.TERRENY'!$K$22)))","v":3.2126035682741021},{"$f":"$D$20+('5.CÀLCUL'!$M$8-$D$20)*(EXP(-($K16))*COS((2*PI()*(1/PARÀMETRES!$D$38))-($K16)))","v":15.831142385958721}]
[null,null,"Oct",{"$f":"'2.CLIMA'!I21","v":17.5},{"$f":"D17+('2.CLIMA'!$K$19-D17)*COS((2*PI()*((365*3600)/PARÀMETRES!$D$38)))","v":30.539998654902423},{"$f":"$D$20+(D17-$D$20)*EXP(-('4.CONDUCTES'!$E$26/(SQRT(('3.TERRENY'!$K$19*PARÀMETRES!$D$38)/(PI()*'3.TERRENY'!$K$16*'3.TERRENY'!$K$22)))))*COS((2*PI()*(1/PARÀMETRES!$D$38))-('4.CONDUCTES'!$E$26/(SQRT(('3.TERRENY'!$K$19*PARÀMETRES!$D$38)/(PI()*'3.TERRENY'!$K$16*'3.TERRENY'!$K$22)))))","v":16.753639402776205},{"$f":"F17-(F17-D17)*EXP(-((3600*'5.CÀLCUL'!$M$23*PI()*'4.CONDUCTES'!$E$30*'4.CONDUCTES'!$E$28)/(PARÀMETRES!$D$30*PARÀMETRES!$D$31*'5.CÀLCUL'!$H$28)))","v":17.334629086669239},null,null,9,{"$f":"J17/(SQRT(('3.TERRENY'!$K$19*PARÀMETRES!$D$38)/(PI()*'3.TERRENY'!$K$16*'3.TERRENY'!$K$22)))","v":3.6141790143083647},{"$f":"$D$20+('5.CÀLCUL'!$M$8-$D$20)*(EXP(-($K17))*COS((2*PI()*(1/PARÀMETRES!$D$38))-($K17)))","v":16.06686565633888}]
[null,null,"Nov",{"$f":"'2.CLIMA'!I22","v":13.5},{"$f":"D18+('2.CLIMA'!$K$19-D18)*COS((2*PI()*((365*3600)/PARÀMETRES!$D$38)))","v":30.403701960058694},{"$f":"$D$20+(D18-$D$20)*EXP(-('4.CONDUCTES'!$E$26/(SQRT(('3.TERRENY'!$K$19*PARÀMETRES!$D$38)/(PI()*'3.TERRENY'!$K$16*'3.TERRENY'!$K$22)))))*COS((2*PI()*(1/PARÀMETRES!$D$38))-('4.CONDUCTES'!$E$26/(SQRT(('3.TERRENY'!$K$19*PARÀMETRES!$D$38)/(PI()*'3.TERRENY'!$K$16*'3.TERRENY'!$K$22)))))","v":15.509432377140984},{"$f":"F18-(F18-D18)*EXP(-((3600*'5.CÀLCUL'!$M$23*PI()*'4.CONDUCTES'!$E$30*'4.CONDUCTES'!$E$28)/(PARÀMETRES!$D$30*PARÀMETRES!$D$31*'5.CÀLCUL'!$H$28)))","v":13.94522938204436},null,null,10,{"$f":"J18/(SQRT(('3.TERRENY'!$K$19*PARÀMETRES!$D$38)/(PI()*'3.TERRENY'!$K$16*'3.TERRENY'!$K$22)))","v":4.0157544603426274},{"$f":"$D$20+('5.CÀLCUL'!$M$8-$D$20)*(EXP(-($K18))*COS((2*PI()*(1/PARÀMETRES!$D$38))-($K18)))","v":16.24796152390568}]
[null,null,"Des",{"$f":"'2.CLIMA'!I23","v":10.199999999999999},{"$f":"D19+('2.CLIMA'!$K$19-D19)*COS((2*PI()*((365*3600)/PARÀMETRES!$D$38)))","v":30.291257186812622},{"$f":"$D$20+(D19-$D$20)*EXP(-('4.CONDUCTES'!$E$26/(SQRT(('3.TERRENY'!$K$19*PARÀMETRES!$D$38)/(PI()*'3.TERRENY'!$K$16*'3.TERRENY'!$K$22)))))*COS((2*PI()*(1/PARÀMETRES!$D$38))-('4.CONDUCTES'!$E$26/(SQRT(('3.TERRENY'!$K$19*PARÀMETRES!$D$38)/(PI()*'3.TERRENY'!$K$16*'3.TERRENY'!$K$22)))))","v":14.482961580991926},{"$f":"F19-(F19-D19)*EXP(-((3600*'5.CÀLCUL'!$M$23*PI()*'4.CONDUCTES'!$E$30*'4.CONDUCTES'!$E$28)/(PARÀMETRES!$D$30*PARÀMETRES!$D$31*'5.CÀLCUL'!$H$28)))","v":11.148974625728837}]
[null,null,"ANUAL",{"$f":"SUM(D8:D19)/12","v":16.416666666666664},{"$f":"SUM(E8:E19)/12","v":30.50308496671558},{"$f":"SUM(F8:F19)/12","v":16.416666666666668},{"$f":"SUM(G8:G19)/12","v":16.416666666666668}]

{"sheet":"DITA","index":8,"n_rows":38,"n_cols":21,"rows_kept":38,"cut":false,"hidden":true,"merged":[]}
[]
["GAEA"]
[]
[null,"Qw= L · ΔTm · ht"]
[]
[]
[null,null,null,null,null,null,null,null,"Temperatura del terreny a la paret del conducte"]
[null,null,null,"Tg1= Tam + (Tamax-Tam) · e-z cos (2π t/t0 -z)",null,null,null,null,"Temperatura del terreny a la paret del conducte sense influència d'aquesta"]
[null,null,null,null,null,null,null,null,"t/t0 = fracció de temps en que t/t0=0 per una temperatura ambient màxima"]
[null,null,null,"to=",{"$f":"365*24*60*60","v":31536000},"s"]
[null,null,null,"t:",{"$f":"24*365*60*60","v":31536000},"s"]
[null,null,null,"x:",2,"m",null,"Te=",31]
[null,null,null,"L:",30,"m",null,"Ta=",{"$f":"E15+(E14-E15)*COS(2*PI()*(E11/E10))","v":31},{"$f":"E15+(E14-E15)*COS(2*PI()*(K14))","v":26.839937968506369},{"$f":"COS(2*PI())","v":1},null,{"$f":"31*24*60*60","v":2678400},null,null,null,"Profunditat","pp","Tg",null,"cos"]
[null,null,null,"Tmax:",31,"ºC",null,"z=",{"$f":"E12*SQRT((PI()*E30*E31)/(E32*E10))","v":0.80046924554346999},{"$f":"E14-E15","v":14.579999999999998},{"$f":"(45/(365))","v":0.12328767123287671},null,null,null,null,null,0,{"$f":"Q14*SQRT((PI()*$E$30*$E$31)/($E$32*$E$10))","v":0},{"$f":"$E$15+($E$14-$E$15)*(EXP(-$R14))*COS((2*PI()*$E$11/$E$10)-R14)","v":31},{"$f":"$E$15+($E$14-$E$15)*(EXP(-$R14))","v":31},{"$f":"COS((2*PI()*$E$11/$E$10)-R14)","v":1}]
[null,null,null,"Tm:",{"$f":"16.42","v":16.420000000000002},"ºC",null,"Tg=",{"$f":"E15+(E14-E15)*(EXP(-I14))*COS((2*PI()*E11/E10)-I14)","v":20.979930371647086},null,null,null,null,null,null,null,1,{"$f":"Q15*SQRT((PI()*$E$30*$E$31)/($E$32*$E$10))","v":0.40023462277173499},{"$f":"$E$15+($E$14-$E$15)*(EXP(-$R15))*COS((2*PI()*$E$11/$E$10)-R15)","v":25.418769586425313},{"$f":"$E$15+($E$14-$E$15)*(EXP(-$R15))","v":26.190973509355757},{"$f":"COS((2*PI()*$E$11/$E$10)-R15)","v":0.92096960224167512}]
[null,null,null,"Tmin:",1.3,"ºC",null,null,null,null,null,null,null,null,null,null,2,0.80046924554346999,20.979930371647086,22.968142888925371,0.69637001650637864]
[null,null,null,"e:",1.4999999999999999E-2,"m",null,"Rcd=",{"$f":"LN((E19+(2*E17))/E19)*(E19+E17+E17)/(2*E38)","v":7.8630898338567901E-2},null,null,null,null,null,null,null,3,1.2007038683152049,18.007263128447253,20.808321721753504,0.36170163198814076]
[null,null,null,"Rad:",{"$f":"E19/2","v":0.15},"m",null,"Rcv=",{"$f":"(E24*E19*PI()*E13)/I21","v":1.5140716638230795E-2},{"$f":"E19/(I21*E24)","v":0.23764496005208435},null,null,null,null,null,null,4,1.60093849108694,16.331368634756871,19.360889937845265,-3.0137600221812489E-2]
[null,null,null,"Diam:",0.3,"m",null,"Rg=",{"$f":"(LN((E19+2*(E17+K19))/(E19+(2*E17)))*(E19+E17+E17))/(2*E32)","v":6.4203479637629679E-2},"ɗ=",{"$f":"SQRT((24*3600*E32)/(PI()*E33*10^6))","v":0.13077927115984092},"(dia)",null,null,null,null,5,2.001173113858675,15.597724812393569,18.390875012113646,-0.41721325936574327]
[null,null,null,"Volum:",1200,"m3",null,null,null,"ɗ=",{"$f":"SQRT((365*24*3600*E32)/(PI()*E33*10^6))","v":2.4985344672950198},"(any)",null,null,null,null,6,2.4014077366304099,15.444790188219665,17.740807101070896,-0.73834385883423048]
[null,null,null,"Cabal:",1200,"m3/h",null,"Nu=",{"$f":"0.0214*((I22^0.8)-100)*(E26^0.4)","v":48.553361013558494},null,null,null,null,null,null,null,7,2.8016423594021451,15.585500592126198,17.305155774727893,-0.9427712406105464]
[null,null,null,"d:",1.2,"kg/m3",null,"Re=",{"$f":"(E27*E19*E22)/(E25)","v":19480.519480519481},null,null,null,null,null,null,null,8,3.2018769821738799,15.827879109141993,17.013198465467731,-0.9981834501057405]
[null,null,null,"ce:",1007,null,null,null,null,null,null,null,null,null,null,null,9,3.6021116049456148,16.063875338491158,16.81753953990917,-0.89582198940566726]
[null,null,null,"λ:",2.5999999999999999E-2,null,null,"Rt=",{"$f":"J18+I17+I19","v":0.38047933802828193},null,null,null,null,null,null,null,10,4.00234622771735,16.246332280859566,16.686416208050343,-0.65186619241882626]
[null,null,null,"mu:",1.8479999999999999E-5,null,null,"Ut=",{"$f":"1/I24","v":2.6282636139512721},null,null,null,null,null,null,null,11,4.4025808504890849,16.365566775825823,16.598542229857539,-0.30487590648785634]
[null,null,null,"Pr:",0.71,null,null,null,null,null,null,null,null,null,null,null,12,4.8028154732608197,16.430805003823458,16.539652359275674,9.0303307756443754E-2]
[null,null,null,"v:",1,"m/s",null,"Qw=",{"$f":"I28*E13*(I17+I18+I19)","v":0},null,null,null,null,null,null,null,13,5.2030500960325545,16.457784637131201,16.500186559177951,0.47120910933897553]
[null,null,null,null,null,null,null,"AT=",null,null,null,null,null,null,null,null,14,5.6032847188042902,16.461788599310655,16.473738048390548,0.77763522424469744]
[null,null,null,"Terreny",null,null,null,"Ts=",{"$f":"I15-(I15-I12)*EXP(-I30)","v":29.31190488288604},null,"k",{"$f":"I25","v":2.6282636139512721},null,null,null,null,15,6.0035193415760251,16.454614043218847,16.456013240553396,0.96114769698453351]
[null,null,null,"d:",1800,null,null,"ξ=",{"$f":"(3600*E19*PI()*E13*I25)/(E21*E22*E23)","v":0.1844895803167331},null,"ntu",{"$f":"(L29*PI()*E19*E13*3600)/(E21*E23*E22)","v":0.1844895803167331}]
[null,null,null,"cp:",1340,null,null,null,null,null,"e",{"$f":"1-EXP(-L30)","v":0.16847139588105298}]
[null,null,null,"λ:",1.5,null,null,null,null,null,"ts",{"$f":"I12+L31*(I15-I12)","v":29.31190488288604}]
[null,null,null,"ρc:",{"$f":"E30*E31/10^6","v":2.4119999999999999}]
[]
[null,null,null,"Conducte"]
[null,null,null,"d:",1400]
[null,null,null,"ce:",1500]
[null,null,null,"λ:",0.2]