© <2017>. This manuscript version is made available under the CC-BY-NC-ND 4.0 license http://creativecommons.org/licenses/by-nc-nd/4.0/

Analysis of thin film photovoltaic modules under outdoor long term exposure in semi-arid climate conditions.

Ali Tahria, Santiago Silvestreb*,  Fatima Tahric,

Soumia Benlebnaa, Aissa Chouderd.

a  Electrical Engineering Faculty of the University of Science and Technology of Oran, Mohamed Boudiaf USTO-MB, BP 1505 El M’naouer, Oran, 31000, Algeria.

alitahri.dz@gmail.com

b MNT Group, Electronic Engineering Department, Universitat Politécnica de Catalunya (UPC) BarcelonaTech, C/Jordi Girona 1-3,Campus Nord UPC, 08034 Barcelona, Spain.

* Corresponding author. Telephone/fax number: +34 93 4017491/+34 93 4016756; email: Santiago.silvestre@upc.edu

c High School of Electrical Engineering and Energetics of Oran, ESGEE, BP 64 CH2 ACHABA HANIFI -USTO- ORAN, Algeria

d Electrical Engineering Laboratory (LGE), University Mohamed Boudiaf of M’sila, BP 166, 28000, 6 Algeria

Abstract

The aim of this paper is to present an analysis of long term outdoor exposure of two thin film photovoltaic (TFPV) module technologies deployed in semi-arid climate in Saida city located in Algeria. The TFPV modules are: a-Si:H/μc-Si:H (micromorph) and copper indium selenide (CIS). The TFPV modules were characterised by measuring their I-V curves during three years under the same outdoor climate conditions, where the measurement of weather parameters were also performed. The goal of the analysis is to evaluate the degradation rates of the TFPV modules in semi-arid climate. The analysis is based on two techniques, the effective peak power of PV module and power irradiance technique. It was found that TFPV modules CIS and micromorph exhibit a degradation rate of -2.34%/year and -1.73%/year respectively. The calculated degradation rate for CIS technology is higher than those reported in the literature for locations in Europe and lower than those for locations with hot and humid conditions. In the opposite the degradation rate of the micromorph was lower than those given in the literature.

Keywords: Thin-film; PV modules; Degradation rate (DR); Semi-arid climate conditions.

- Introduction

The exponential growth of the Photovoltaic (PV) market has been maintained from more than a decade. The global PV installed capacity in 2015 total is 228 GW and it is expected to follow its growth in the next years because of the trends observed in China, Japan and the United States (USA) among other countries (IEA, 2016).

Global PV module production is clearly dominated by crystalline silicon PV and in second place by thin-film (TF) PV. It is estimated that 3.6 GW of TFPV modules were produced in 2015, accounting for 6% of total PV module production (IEA, 2016). Despite TFPV modules have reduced its market share in a 4% from 2014, its annual production as increased in 1.2 GW last two years (Institute for Solar Energy Systems, 2016).

TFPV modules present lower production costs and lower temperature coefficients relative to the crystalline (c-Si) and polycrystalline silicon PV modules (Virtuani et al., 2010; Tossa et al., 2016). Therefore, TFPV modules are especially attractive in applications where high ambient temperatures are reached.

The most common materials used in the production of TFPV modules are copper indium gallium selenide sulphide (Cu(In,Ga)Se2, CIGS), cadmium telluride (CdTe), and amorphous silicon (a-Si). These PV technologies present lower efficiencies than c-Si based PV modules. However, the efficiency of TFPV modules has significantly improved. CIGS and CuInSe2 (CIS)-based PV modules passed from 14.2 % conversion efficiency (Kushiya, 2014) to 17.5 % (Institute for Solar Energy Systems, 2016) and First Solar has achieved 22.1% of  conversion efficiency in CdTe TFPV modules in the laboratory (IEA, 2016).  Moreover, the theoretical conversion efficiency limit for CdTe TFPV modules is 29% due to their band gap of 1.45 eV (Muñoz-García et al., 2012).

However, TFPV modules present degradation phenomena when exposed outdoor  (Meyer and van Dyk, 2003; Mendoza-Pérez et al., 2009; Muñoz-García et al., 2012; Jordan and Kurtz, 2013;). Staebler-Wronski effect (SWE) causes light induced degradation (LID) that strongly affects hydrogenated amorphous silicon (a_Si:H) and it also has effects, although more reduced in amorphous silicon/hydrogenated microcrystalline silicon heterojunction  (a-Si:H/µc-Si:H), also called micromorph TFPV modules (Staebler and Wronski, 1977; Yamawaki et al., 1997; Van Dyk et al., 2007).

Several studies of TFPV modules were recently presented in the literature including, life cycle assessment (Chatzisideris et al., 2016), effects of irradiance change on the values of model parameters of a_Si:J TFPV modules (Elbaset et al., 2016) and analysis of the performance ratio (PR) of CdTe, a_Si:H, micromorph and CIS TFPV modules (Moreno-Sáez, 2016 ; Balaska et al., 2017). Moreover, the performance evaluation and degradation analysis of micromorph, a-Si:H, CIS and CdTe was also recently reported in several climate conditions (Aste et al., 2014; Kichou et al., 2016a; Silvestre et al., 2016; Kichou et al., 2016b; Rawat el al., 2017). The selection of the best TFPV technology for each specific climate condition is crucial in order to improve the energy generated by PV systems.

This work presents an analysis of two TFPV module technologies under outdoor long term exposure in semi-arid climate conditions. Three years was the period of the study, from January 2014 to December 2016.

The paper is organised as follows: Section 2 gives a description of the methodology by detailing the TFPV modules, the monitoring system and the techniques used to analyse the behaviour of the TFPV modules. Section 3   presents the results and discussion of the degradation and stabilisation period of each technology. Finally, in section 4, the most important conclusions are summarised.

- Methodology

2.1 	Description of the PV modules and monitoring system

The two PV modules considered in this work correspond to the following TF technologies: a-Si:H/μc-Si:H (micromorph) and copper indium selenide (CIS).  The main parameters of the TFPV modules at standard test conditions (STC): G=1000 W/m2 AM1.5G, Tc=25C, used in this study are given in Table 1.

|  | PV module |  |
| --- | --- | --- |
|  | Sharp NA-121 | Solar Frontier SF150-S |
| Technology | a-Si:H/μc-Si:H | CIS |
| Peak power (W) | 110 | 150 |
| Voltage at nominal power (V) | 53.5 | 81.5 |
| Current at nominal power (A) | 2.04 | 1.85 |
| Isc (A) | 2.5 | 2.2 |
| Voc(V) | 71 | 108 |
| Temperature coefficient- power δ (%/C) | -0.35 | -0.31 |
| Temperature coefficient- Voltage (%/C) | -0.39 | -0.3 |
| Temperature coefficient- current (%/C) | 0.056 | 0.01 |
| Efficiency (%) | 9 | 12.2 |

Table 1. Main parameters of PV modules obtained from

the manufacturers' data sheet.

The two TFPV module technologies were installed at the University of Saida in Algeria. Saida city is located between the north and the south of Algeria near the border of high plateaux with an altitude of 868 m, latitude: 34° 49' 60'' north and longitude 0° 9' east. The TFPV modules were mounted at the University of Saida faced to south with a tilt angle of 30°. Saida is renowned by its semi-arid climate with influences of Saharan climate especially in the summer.

The monitoring system was set to scan the electrical and meteorological parameters every 10 min. The electrical parameters of the PV modules were obtained by measuring their I-V curves by a system based on capacitor load. The I-V curve measurement system is synchronised to a weather station which allows recording the meteorological parameters to CR1000 data logger from Campbell Scientific. The irradiance was measured using HukseFlux SR20 Pyranometer wit tilt response <0.2 % (0 to 90° at 1000 W/m2 ), the ambient temperature and relative humidity were sensed by Vaisala HMP155 probe with temperature and relative humidity accuracy of 0.20 °C and 1.7% respectively. The wind speed and direction were measured by Young 05106 sensor with an accuracy of 0.3 m/s and 3 degrees of wind direction. The T type thermocouple cables attached to the back surface of the modules were used to sense the modules temperature and are also recorded with the environmental parameters by the CR1000 data logger.

The annual daily average and the standard deviation values of meteorological parameters recorded in sun hours during the monitoring campaign are summarised in Table 2 and Fig. 1 .

|  |  | Irradiation (kWh/m2) |  | Ambient temp. (°C) |  | Rel. Humidity (%) |  | Wind speed (m/s) |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  | Mean | STD | Mean | STD | Mean | STD | Mean | STD |
| 2014 | Jan-14 | 3.35 | 1.63 | 11.71 | 2.95 | 59.16 | 15.59 | 1.74 | 0.85 |
|  | Fev-14 | 4.36 | 1.99 | 12.80 | 3.75 | 57.70 | 17.61 | 1.93 | 0.54 |
|  | Mar-14 | 5.49 | 2.19 | 13.48 | 2.94 | 54.31 | 15.42 | 1.79 | 0.82 |
|  | Apr-14 | 6.79 | 1.41 | 20.56 | 3.70 | 38.99 | 11.91 | 1.68 | 0.78 |
|  | May-14 | 7.17 | 1.11 | 23.00 | 3.24 | 37.11 | 12.34 | 1.51 | 0.32 |
|  | Jun-14 | 6.78 | 1.45 | 26.06 | 4.47 | 36.24 | 15.97 | 1.55 | 0.41 |
|  | Jul-14 | 6.67 | 1.14 | 29.98 | 2.94 | 28.89 | 8.00 | 0.96 | 0.60 |
|  | Aug614 | 6.40 | 0.89 | 31.50 | 2.06 | 27.36 | 6.75 | 0.001 | 0.01 |
|  | Sep-14 | 4.98 | 1.85 | 27.57 | 3.31 | 39.08 | 13.32 | 0.80 | 0.48 |
|  | Oct-14 | 5.62 | 1.58 | 23.36 | 3.24 | 38.97 | 14.63 | 0.94 | 0.53 |
|  | Nov-14 | 3.26 | 1.67 | 15.97 | 3.47 | 59.00 | 16.20 | 1.20 | 0.94 |
|  | Dec-14 | 3.62 | 1.54 | 10.51 | 2.49 | 63.11 | 11.97 | 1.13 | 0.77 |
|  | Annual | 5.37 | 1.54 | 20.54 | 3.21 | 44.99 | 13.31 | 1.27 | 0.59 |
| 2015 | Jan-15 | 3.94 | 1.63 | 10.65 | 4.05 | 56.78 | 17.17 | 0.93 | 0.73 |
|  | Fev-15 | 2.86 | 1.61 | 8.71 | 2.52 | 69.32 | 11.39 | 1.47 | 0.82 |
|  | Mar-15 | 5.98 | 1.60 | 14.59 | 3.69 | 51.48 | 13.20 | 0.98 | 0.51 |
|  | Apr-15 | 6.67 | 0.99 | 20.95 | 2.22 | 40.83 | 13.13 | 1.12 | 0.62 |
|  | May-15 | 6.47 | 1.86 | 24.83 | 5.30 | 34.75 | 18.57 | 1.17 | 0.60 |
|  | Jun-15 | 6.49 | 1.50 | 25.74 | 4.23 | 38.86 | 15.08 | 0.84 | 0.35 |
|  | Jul-15 | 7.10 | 0.78 | 33.55 | 1.56 | 22.64 | 5.94 | 1.00 | 0.31 |
|  | Aug-15 | 6.03 | 1.06 | 31.17 | 3.07 | 34.27 | 9.73 | 0.89 | 0.30 |
|  | Sep-15 | 6.18 | 1.45 | 25.68 | 2.59 | 42.13 | 11.33 | 0.83 | 0.32 |
|  | Oct-15 | 5.08 | 1.77 | 21.59 | 3.74 | 55.08 | 15.37 | 0.62 | 0.43 |
|  | Nov-15 | 4.93 | 1.38 | 15.68 | 3.57 | 57.95 | 11.10 | 0.73 | 0.70 |
|  | Dec-15 | 4.58 | 1.14 | 14.96 | 1.87 | 41.87 | 7.14 | 0.87 | 0.50 |
|  | Annual | 5.53 | 1.40 | 20.68 | 3.20 | 45.50 | 12.43 | 0.95 | 0.51 |
| 2016 | Jan-16 | 4.30 | 1.48 | 14.39 | 2.83 | 48.00 | 13.24 | 1.21 | 0.56 |
|  | Fev-16 | 4.37 | 1.77 | 13.56 | 4.30 | 52.36 | 16.08 | 1.52 | 0.62 |
|  | Mar-16 | 5.81 | 2.00 | 13.23 | 4.55 | 55.16 | 15.02 | 1.24 | 0.51 |
|  | Apr-16 | 5.97 | 1.96 | 17.77 | 3.95 | 53.97 | 14.35 | 1.23 | 0.55 |
|  | May-16 | 5.98 | 1.78 | 21.85 | 4.37 | 44.85 | 15.55 | 1.23 | 0.37 |
|  | Jun-16 | 6.79 | 1.20 | 28.06 | 3.76 | 29.28 | 8.68 | 1.15 | 0.32 |
|  | Jul-16 | 6.35 | 1.15 | 32.88 | 2.67 | 26.34 | 8.30 | 1.23 | 0.44 |
|  | Aug-16 | 6.88 | 1.07 | 31.04 | 2.77 | 31.00 | 8.33 | 1.16 | 0.39 |
|  | Sep-16 | 5.64 | 1.60 | 26.97 | 4.60 | 36.28 | 12.92 | 0.98 | 0.32 |
|  | Oct-16 | 5.37 | 1.45 | 24.59 | 3.01 | 35.15 | 7.88 | 1.00 | 0.46 |
|  | Nov-16 | 3.77 | 1.83 | 15.17 | 4.26 | 53.47 | 19.55 | 1.25 | 0.58 |
|  | Dec-16 | 3.49 | 1.93 | 12.13 | 2.39 | 66.76 | 13.69 | 0.80 | 0.45 |
|  | Annual | 5.39 | 1.60 | 20.97 | 3.62 | 44.39 | 12.80 | 1.17 | 0.46 |

Table 2. : Monthly daily average and annual daily average values of the meteorological parameters and their relative standard deviations during the monitoring campaign.

Fig. 1. PV module temperatures along the monitoring campaign.

Fig. 1 shows the PV modules temperatures: Average, minimum and maximum in monthly average values along the monitoring campaign. As it can be seen in the figure, the CIS PV module presents always higher temperatures than the micromorph PV module.

2.2 Effective peak power of the PV modules

The analysis of the behaviour of the output power of the PV modules is based in the application of two techniques described in this section: The evaluation of the effective peak power and the power-irradiance technique.

The effective peak power of a PV module, P*M, is given by the following equation (Martinez-Moreno et al.,2012; Nofuentes et al., 2006) :

PM*=G*PDCGTf		(1)

where PDC, G and G* are the DC output power of the PV module, the irradiance, and irradiance at STC respectively. Tf is the thermal factor defined as follows:

Tf=11+δTm-Tm*		(2)

where Tm is the PV module temperature, Tm* is the module temperature at STC  and 𝛿 is the power temperature coefficient of the PV modules given in Table 1.

The evaluation of P*M was carried out as the product of the normalized values of the MPP current, Imn, and voltage, Vmn, obtained from the following equations [Limmanee et al., 2016]:

Imn=Im (G*G)1+ Tm-Tm*		(3)

Vmn=Vm 1+ Tm-Tm*		(4)

vhere Im and Vm are the measured current and voltage at the MPP,  and  are the current and voltage temperature coefficients of the PV modules respectively.

The evaluation of P*M from the monitoring data set was performed after disregarding data recorded at low irradiance values. Only measurements taken at G > 700 W/m2 were used. Above this irradiance threshold the shape of varying solar spectra closely resembles that of the spectral AM1.5G reference spectrum [Silvestre et al., 2016]. Consequently, no spectral effects are taken into account in Eq. (1).

The degradation rate, DR (%/year), of the TFPV modules is evaluated by means of a linear least square fitting method of the P*M by using Eq. (5).

DR=10012b a		(5)

where b (W/month) is the slope of line and a (W) is the y intercept of the trend line obtained for  P*M  (Sharma et al., 2014; Malvoni et al., 2017):

y=a+ bx		(6)

2.3 Power-Irradiance technique

The power-irradiance technique is the method used in this work to analyze the stabilization period of the TFPV modules. This method was proposed by Hussin et al. (Hussin et al.,2015) and was applied with success in several works reported in the literature to study the degradation of TFPV modules (Kichou et al., 2016a; Kichou et al. 2016b).

Linear regression equations from the actual PV modules DC outputs, PDC, as a function of the irradiance, G, are evaluated by using the following equation:

PDC=AGr.G+C		(7)

where PDC is the PV module DC output power, AGr,  is the gradient, G is the plan-of-array irradiance and C is the ordinate value of PDC at G = 0.

The data filtering process introduced in the previous section was also used in the development of the power-irradiance technique in order to avoid problems caused by low values of irradiance (G<700 W/m2).

The determination of the stabilization period of the PV modules is based in the monthly values of the gradients, AGr, corresponding to the empirical equations obtained in the process along the monitoring campaign [Hussin et al., 2015]. When the values of AGr remain constant or present symmetrical seasonal oscillations respect to an average value it is considered that the PV module is stabilized.

2.4 Performance evaluation of the PV modules

In order to analyze the performance of TFPV modules, the performance ratio is calculated monthly average daily. Performance ratio, PR, is calculated for each technology as recommended in IEC61724 Standard (Standard IEC 61724, 1998).

PR%=YYr.100		(8)

where Y is the yield which represents the number of hours in which the PV module would need to operate at its rated power defined as follows:

Y=EPMSTC			(9)

where E is the energy produced by each PV module and PMSTC is the measured maximum power under standard test conditions STC. Yr is the reference yield and it is expressed as follows :

Yr=τGG*			(10)

where  is the recording interval.

- Results and discussion

  - Evolution of the effective peak power of the PV array

The evolution of the effective peak power, P*M, of the CIS PV module calculated by using the Eq. 1 and monitored data is plotted in Fig. 2, as well as the monthly average values of the measured irradiance above the fixed threshold. The decrease rate of P*M is clearly observed. The power reduction at the last month of the monitoring campaign respect to the initial value is 3.25 %, this value is a little bit higher than the observed after a period of 3 years in Madrid for CIS PV modules, where the DC output power value was decreased of 2.66% [Silvestre et al., 2016]. However, the same 3.25 % reduction of P*M is achieved at the beginning of the second year of outdoor exposure of the CIS PV module. Moreover, a slight seasonal variation up to 5% can be observed in the trend of P*M due to irradiance and temperature effects.

The degradation rate calculated from the trend line by using Eqs. 3 and 4 is found to be: -2.34%/year. Previous works carried out in different locations provide DR values of -0.5%/year in the temperate climate of Germany (Jordan and Kurtz, 2013),- 1.04%/year under Madrid climate (Silvestre et al., 2016) and signiﬁcant higher values of -5.13%/year and -4.57%/year in Florida (Phinikarides, A. et al., 2014), where the potential induced degradation (PID) is accelerated under hot and humid conditions (Dhere et al. 2012). The DR obtained in the semi-arid climate of the city of Saida Algeria is higher than values reported in Berlin and Madrid climates and lower than values reported in humid climates.

Fig. 2. Evolution of P*M of the CIS PV module.

The evolution of the output current at the maximum power point, Im, of the CIS PV module, monthly average values, is depicted in Fig. 3 as well as the irradiance profile. As it can be seen in the figure, the evolution of Im is in accordance with the irradiance profile and presents variations up to 10% respect to the average value of 1.47 A.

Fig. 3. Irradiance and Output current Profiles. Monthly filtered average values.

Fig. 4 shows the evolution of the output voltage at the maximum power point, Vm, for the CIS PV module and the temperature profile along the monitoring campaign, monthly average values. The reduction observed in the Vm of the CIS PV module shows a similar trend to the one observed in the evolution of the effective peak power given in Fig. 2 and seems to be the  responsible of the output power overall reduction. Moreover, a seasonal fluctuation of Vm is also observed. As it can be seen in Fig. 4, the seasonal behaviour is clearly due to temperature effects. The evolution of Vm is in accordance with the temperature profile and presents variations up to 4.9 respect to the average value of 77.35 V.

Fig. 4.Temperature and Output voltage of the PV module, monthly average values after the filtering process.

The DR of the micromorph PV module is found to be -1.73 %/year, lower than the DR of the CIS PV module and below values reported in previous works of -2.2%/year (Kichou et al., 2016b) and -2.72%/year (Silvestre et al. 2016) in Spain.

Fig. 5. Evolution of P*M for the micromorph

PV module.

The result obtained by applying the filtering process of restricted interval of solar irradiance is shown in Fig. 5. The values of P*M are monthly average values. The power reduction at the las month of the monitoring campaign respect to the initial value is 3.1%, similar to the reduction of P*M observed at the end of the first year of outdoor exposure. Moreover, a slight seasonal variation up to 9.5% respect the average value of 106.81 W can be observed in the trend of P*M due to irradiance and temperature effects. The seasonal variation is more important in the micromorph than in the CIS TFPV module as result of its higher temperature coefficient of power and also to the LID that affects the top amorphous layer of the solar cells forming the PV module.

Fig. 6. Micromorph PV module:

Monthly filtered average values of Irradiance and output current.

Fig. 6 shows the evolution of the output current at the maximum power point, Im, of the micromorph PV module and the irradiance profile, monthly average values. As it can be seen in the figure, the evolution of Im follows the irradiance profile and presents variations up to 14% respect to the average value of 1.78 A. Moreover, temperature effects also are present in the trend of Im due to the high value of the current temperature coefficient of this PV module.

Fig. 7.Temperature profile and maximum output voltage of the micromorph PV module, monthly average values after the filtering process.

The evolution of the output voltage at the maximum power point, Vm, for the micromorph PV module and the temperature profile along the monitoring campaign, monthly average values, is shown in Fig. 7. The reduction observed in the Vm of the micromorph PV module shows a similar trend to the one observed in the evolution of the Vm for the CIS PV module. This can be explained by the similar values of temperature coefficient of voltage of both PV modules.

Moreover, a seasonal fluctuation of Vm is also observed as in the case of the CIS PV module. As it can be seen in Fig. 7, the seasonal behaviour is again clearly due to temperature effects. The evolution of Vm is inverse of the temperature profile and presents variations up to 4.5% respect to the average value of 49 V.

  - Analysis of Stabilization Period

The analysis of the stabilization period of the micromorph PV module is carried out by following the power-Irradiance method described in section 2.3.

From the plots of the monthly PDC as a function of irradiance, the trend line defined by Eq. (7) is extracted with a linear correlation approach (LCA). Fig. 8 shows the plot of PDC and the trend line obtained for the micromorph PV module in June of 2015, where a value of the gradient, AGr, of 0.097 is observed.

Fig. 8. PDC as a function of irradiance and trend line.

The stabilization period can be analysed by plotting the gradient values, AGr, obtained from Eq. (7) (Hussin et al., 2015; Kichou et al., 2016a; Kichou et al. 2016b).  Fig. 9 shows the evolution of the AGr values obtained along the monitoring campaign for the micromorph and CIS PV modules.

As it can be seen in the figure, the AGr values obtained for the CIS PV module do not show a significant degradation until the last seven months of the monitoring campaign.

Fig. 9. Plot of the gradients, AGr, for the micromorph and CIS PV modules.

Concerning the micromorph TFPV module, the evolution of the AGr values shows an initial decrease and then keeps decreasing with a seasonal variation. However, after the first four months of operation, the evolution of the AGr values is quite stable. Stabilization periods reported in previous works for micromorph TFPV modules range from few weeks to four months (Hussin et al., 2015; Kichou et al., 2016b). Seasonal effects are more clear in this case, a rise of the AGr values is observed during the winter months due to the temperature effects in the µc-Si:H layer.

  - Fill Factor and Performance Ratio

The evolution of the fill factor, FF, along the monitoring campaign is depicted in Fig. 10. The FF was evaluated by using monthly average values of the parameters monitored for irradiance levels over 700 W/m2 by means of the following equation:

FF=PmVoc  Isc 			(11)

where Isc and Voc are the short-circuit current and open circuit voltage of the PV modules respectively and Pm is the maximum power point.

Fig. 10. Evolution of the FF for CIS and micromorph TFPV modules.

The FF of the CIS TFPV module is higher than the FF of the micromorph TFPV module and shows a seasonal oscillation around an average value of 68.2%. It can be observed that the CIS TFPV module performs better during winter months. Moreover, the values of the FF seem to be quite stable and present higher values at the latest months of the monitoring period.

This improvement in the FF can be explained by analysing the evolution of the relationships between the voltage, Vm, and current, Im, of the maximum power point respect to the values monitored for Voc and Isc. Fig. 11 shows the profiles of both parameters:

VmVoc			(12)

and

ImIsc			(13)

The FF is obtained as the product of Eqs. 12 and 13, as it was described in Eq. 11. As it can be seen in Fig. 11, the evolution of the relationship between Vm and Voc reflects the degradation observed in the output power of the PV module and the seasonal variations due to temperature effects. The trend of the relationship between Im and Isc indicate that the reduction of Im is lower than the reduction of Isc, especially in the last months of the monitoring campaign, in accordance with the evolution of P*M shown by Fig. 1 for the CIS TFPV module. This is the reason because the FF present maximum values the latest months in Fig. 10.

Fig.11. Evolution of the relationships: Vm/Voc and Im/Isc

for the CIS TFPV module.

The evolution of the FF of the micromorph TFPV module shows the opposite trend to the observed in the case of the CIS PV module. A clear reduction, with seasonal variations due to the LID effect that improves the output current of the PV module in summer months, is observed in Fig. 10.

Fig. 12. Evolution of the PR for CIS and micromorph PV modules.

The evolution of the monthly average daily PR of the two TFPV modules is shown in Fig. 12. As it can be seen in the figure, the CIS PV module performed better than the micromorph PV module. The degradation of the PR along the monitoring campaign is observed in both technologies.

Fig. 13. Normalized PR with temperature compensation.

The normalized PR with temperature compensation (Ueda et al., 2009; Limmanee et al., 2017), monthly average daily, is shown in Fig. 13 for both TFPV modules. The normalized PR with module temperature compensation of both PV modules tended to decrease with increasing operation time. The CIS PV module performs better the first months of outdoor exposure but at the last two years of the monitoring campaign the micromorph PV module shows the best performance due to its lower value of DR.

Finally, Figs. 14 and 15 show the normalized frequency of the PR values along the monitoring campaign for the CIS and micromorph PV modules respectively. In these figures it can be seen again that the micromorph PV module performed better than the CIS one along the period analyzed. 98% of the performance ratio for Micromorph took place between 85 % and 105 %  but in the case of the CIS and for the same interval, just 85% occurred.

Fig. 14. Normalised frequency of the PR for the CIS PV module.

Fig. 15. Normalised frequency of the PR for the micromorph PV module.

- Conclusion

The behavior of micromorph and CIS TFPV modules under outdoor long term exposure in semi-arid climate conditions was analyzed from January 2014 to December 2016.

The evolution of the effective peak power, P*M, of both PV modules shows a similar power reduction around 3% at the end of the monitoring campaign.

Moreover, seasonal variations, up to 5% for the CIS module and 9.5% for the micromorph module, respect the average values are observed in the trends of P*M basically due to temperature effects. The seasonal variation is more important in the micromorph than in the CIS module as result of its higher temperature coefficient of power and also to the LID effect.

The micromorph module has a higher value of the current temperature coefficient than the CIS module. Therefore, the evolution of the output current at the maximum power point, Im, of the CIS PV module presents variations up to 10% respect its average value, while these variations are up to 14% in the micromorph module. Concerning the output voltage at the maximum power point, Vm, a seasonal behavior is observed in both PV modules due to temperature effects. Indeed, CIS and micromorph modules have similar values of temperature coefficient of voltage.

The DR obtained for the CIS PV module is -2.34%/year. It is higher than the DR evaluated for the micromorhp PV module of -1.43%/year and also higher than values reported in Berlin and Madrid climates but lower than values reported for CIS PV modules deployed in humid climates.

The CIS module presents better FF than the micromorph module. Seasonal variations are also observed in the values of the FF for both PV modules. The CIS module performs better during winter months, while the micromorph module shows the opposite trend due to the LID effect that improves the output current of the PV module in summer months.

References

Niccolò Aste, Claudio Del Pero, Fabrizio Leonforte, 2014. PV technologies performance comparison in temperate climates. Solar Energy 109:  1-10.

Balaska A, Tahri A, Tahri F, & Stambouli, AB, 2017. Performance
      assessment of five different photovoltaic module technologies under
      outdoor conditions in Algeria. Renewable Energy, 107:53-60.

Chatzisideris MD, Espinosa N, Laurent A, & Krebs FC, 2016. Ecodesign perspectives of thin-film photovoltaic technologies: A review of life cycle assessment studies. Solar Energy Materials and Solar Cells, 156: 2-10.

Dhere N, Kaul A, Schneller E, Shiradkar N. High-voltage bias testing of PV modules in the hot and humid climate without inducing irreversible instantaneous degradation. In: Proceedings of the 38th IEEE photovoltaic specialists conference; 2012. p. 2445–8.

Elbaset AA, Ali H, & El Sattar MA, 2016. New seven parameters model for amorphous silicon and thin film PV modules based on solar irradiance. Solar Energy, 138: 26-35.

Fraunhofer Institute for Solar Energy Systems, ISE. Photovoltaics Report. Freiburg, 11 March 2016. https://www.ise.fraunhofer.de/de/downloads/pdf-files/aktuelles/photovoltaics-report-in-englischer-sprache.pdf

Hussin MZ, Shaari S, Omar AM, Zain ZM, 2015. Amorphous silicon thin-film: behaviour of light-induced degradation. Renew Sustain Energy Rev 43:388–402

IEA International Energy Agency. 2016. Trends 2016 in photovoltaic applications. Report IEA PVPS T1-30:2016. ISBN 978-3-906042-45-9. http://iea-pvps.org/fileadmin/dam/public/report/national/Trends_2016_-_mr.pdf

Jordan DC, Kurtz, SR, 2013. Photovoltaic degradation rates - An Analytical Review. Prog. Photovoltaics Res. Appl. 21: 12–29.

Kichou S, Silvestre S, Nofuentes G, Torres-Ramírez M, Chouder A, Guasch D, 2016a. Characterization of degradation and evaluation of model parameters of amorphous silicon photovoltaic modules under outdoor long term exposure. Energy, 96: 231-241.

Kichou S, Abaslioglu E, Silvestre S, Nofuentes G, Torres-Ramírez M, Chouder A, 2016b. Study of degradation and evaluation of model parameters of micromorph silicon photovoltaic modules under outdoor long term exposure in Jaén, Spain. Energy Conversion and Management  120:109–119.

Kushiya, K, 2014. CIS-based thin-film PV technology in solar frontier KK. Solar Standard, I. E. C. (1998). 61724. IEC: Geneva, Switzerland. Energy Materials and Solar Cells, 122: 309-313.

Limmanee A, Udomdachanut N, Songtrai S, Kaewniyompanit S, Sato Y, Nakaishi M, Kittisontirak S, Sriprapha Y, Sakamoto, Y, 2016. Field performance and degradation rates of different types of photovoltaic modules: a case study in Thailand. Renewable Energy, 89, 12-17.

Limmanee A, Songtrai S, Udomdachanut N, Kaewniyompanit S, Sato Y, Nakaishi M, Kittisontirak S, Sriprapha K, Sakamoto Y, 2017.Degradation analysis of photovoltaic modules under tropical climatic conditions and its impacts on LCOE. Renewable Energy 102, 199-204.

Malvoni M, Leggieri A, Maggiotto G, Congedo PM, & De Giorgi M G, 2017. Long term performance, losses and efficiency analysis of a 960kW P photovoltaic system in the Mediterranean climate. Energy Conversion and Management, 145, 169-181.

Martínez-Moreno F, Lorenzo E, Muñoz J, Moretón R, 2012. On the testing of large PV arrays. Prog. Photovoltaics Res. Appl. 20:100–5.

Mendoza-Pérez R, Sastre-Hernández J, Contreras-Puente, G and Vigil-Galán O, 2009. CdTe solar cell degradation studies with the use of CdS as the window material. Solar Energy Materials & Solar Cells 93(1): 79-84.

Meyer EL, van Dyk EE, 2003. Characterization of degradation in thin-film photovoltaic module performance parameters. Renew. Energy 28: 1455–1469.

Moreno-Sáez R, Sidrach-de-Cardona M, & Mora-López L, 2016. Analysis and characterization of photovoltaic modules of three different thin-film technologies in outdoor conditions. Applied Energy, 162, 827-838.

Muñoz-García M, Marin O, Alonso-García MC, Chenlo F, 2012. Characterization of thin film PV modules under standard test conditions: Results of indoor and outdoor measurements and the effects of sunlight exposure. Sol. Energy 86: 3049–3056.

Nofuentes G, Aguilera J, Santiago RL, De La Casa J, Hontoria L. 2006; A reference-module-based procedure for outdoor estimation of crystalline silicon PV module peak power. Prog Photovoltaics Res Appl. 14: 77–87.

Phinikarides A, Kindyni N, Makrides G, Georghiou GE, 2014.  Review of photovoltaic degradation rate methodologies. Renew. Sustain. Energy Rev. 40: 143–152.

Rawat R, Singh R, Sastry OS, & Kaushik SC, 2017. Performance
evaluation of micromorph based thin film photovoltaic modules in real operating conditions of composite climate. Energy, 120: 537-548.

Sharma V, Sastry OS, Kumar A, Bora B, Chandel SS, 2014. Degradation analysis of a-Si, (HIT) hetro-junction intrinsic thin layer silicon and m-C-Si solar photovoltaic technologies under outdoor conditions. Energy 72:536-546.

Silvestre S, Kichou S, Guglielminotti L, Nofuentes G, Alonso-Abella M, 2016. Degradation analysis of thin film photovoltaic modules under outdoor long term exposure in Spanish continental climate conditions. Sol Energy 139:599–607.

Staebler D, Wronski C, 1977. Reversible conductivity changes in discharge-produced amorphous Si. Appl Phys Lett 31(4):292-294.

Standard, I. E. C. (1998). 61724. IEC: Geneva, Switzerland.

Tossa Alain K, Y.M. Soro YM, Thiaw L, Azoumah Y, Lionel Sicot, Yamegueu D. Claude Lishou, Coulibaly Y, Guillaume Razongles, 2016. Energy performance of different silicon photovoltaic technologies under hot and harsh climate. Energy 103 : 261–270.

Ueda Y, Kurokawa K, Kitamura K, Yokota, Akanuma K, Sugihara H, 2009. Performance analysis of various system configurations on grid connected residential PV systems, Sol. Energy Sol. Cells 93, 945-949.

Van Dyk EE, Audouard A, Meyer EL, Woolard CD, 2007. Investigation of the degradationof a thin-film hydrogenated amorphous silicon photovoltaic module. Solar Energy Materials & Solar Cells 91:167-73.

Virtuani A, Pavanello D, Friesen G. Overview of temperature coefficients of different thin film photovoltaic technologies. 25th European photovoltaic solar energy conference and exhibition/5th World conference on photovoltaic energy conversion. Proc. 2010; 6-10.

Yamawaki T, Mizukami S, Yamazaki A, Takahashi H, 1997. Thermal recovery effecton light-induced degradation of amorphous silicon solar module under thesunlight. Solar Energy Materials & Solar Cells 47:125-34.